## Intro
Energy MAP
Best Practice Worksheet - Motors
Version 4
This Best Practice Worksheet for Motors is for identifying and quantifying energy savings opportunities associated with the operation of motors.
Your organisation should continuously identify opportunities for energy savings and record them in the Register of Opportunities. There should be a clear link between the opportunities and the Significant Energy Users in your organisation, e.g. motors.
Layout of this Tool
- Green worksheets: this is where you enter data
- Blue worksheets: summary or example data
- Red worksheets: For SEAI use only
Using this Tool
- | Enter data in the green cells only
- | Each worksheet contains information, tips and calculation methods and examples for a different savings opportunity
Additional Information & Support
- There is extensive guidance on all twenty Energy MAP steps at www.seai.ie/energymap (click here)
- Click here to see SEAI's suite of supports to help public bodies reach their 33% energy-efficiency targets by 2020
- Click here to see SEAI's supports for SMEs and Large Industry

## ReadMe
The "Onion" Approach to Improving Energy Efficiency
1 | Start at the centre of the Onion (see diagram below) by identifying the relevant Energy Service. An energy service demand is the need for a specific level of work or activity to be performed. However, an Energy Service is more than simply 'motive power'. To identify the Energy Service, ask yourself: - What do I want to do with the motor? - What is the fundamental piece of work that I want the motor to do? An example of a motor related Energy Service might be: to drive a conveyor belt to move products from one machine to another.
2 | Then, for each Energy Service, ask yourself: - Do I really need (paid-for) energy to deliver this energy service? - Is there another way of delivering the output that requires using less or no energy? - Can I use a less energy intensive alternative? - What is the minimum specification required? - Can I reduce (increase) pressures, temperatures, run times, flowrates, currents etc. to reduce the energy required?
3 | Start at the point of energy service demand and work back upstream through the energy distribution and conversion system(s) – this is consistent with the energy efficiency hierarchy.
4 | Is the technology that is currently satisfying each energy service demand appropriate? Or can it be eliminated or replaced by a more effective alternative?
5 | Can the system be designed better?
6 | Identify the most efficient / optimum operational control parameters for the most effective technology to satisfy each service demand. Can cycle times be adjusted?
7 | Are there opportunities to distribute the energy more efficiently, e.g. insulation, improved structural integrity (elimination of leaks), isolation etc.?
8 | Is there scope for technical or operational modifications to the energy conversion systems (compressors, boilers, chillers etc.) to reduce the consumption of energy resources (natural gas, gasoil, electricity, wood chips etc.)?
9 | Finally, are there O&M or housekeeping actions that can be taken to reduce the consumption of energy resources?
10 | The following Onion diagram illustrates this approach and also identifies some best practice energy savings measures at different 'layers'. Simple energy saving calculation sheets for each of these measures are included in this spreadsheet.
11 | The Triple E Products Register is a new benchmark register of best in class energy efficient products. Products on this register all meet a minimum set of stringent efficiency criteria and typically will be of a best in class efficiency standard. As such, procuring against this register will provide you with the assurance that you are purchasing a product of very high efficiency. For more information go to www.seai.ie/triplee. Public bodies are obliged to only procure equipment or vehicles that are listed on the register (or equivalent).
12 | SEAI operates an accelerated capital allowance (ACA) scheme, which is a tax incentive for companies that pay corporation tax to purchase energy efficient equipment. It allows companies to write off 100% of the purchase value of specified energy efficient equipment in the year of purchase. To see which equipment qualifies for ACA and to find out more go to www.seai.ie/aca or click on the graphic below. There is also useful technical information available on the qualifying equipment. There is also an ACA worksheet in this spreadsheet.

## Switching Off
Motors - Switching Off
Motors use no energy when switched off. Reducing motor operation by 10% can usually result in larger savings than replacing the motor with an energy efficient motor. Given that 97% of the life cycle cost of buying and running a motor is energy-related, switching off a motor for 10% of the time could amount in enough energy savings to buy three motors.
Estimate Your Savings
What Does this Sheet Do? This sheet calculates the energy savings achievable by switching off motors when not in use.
Parameter |  | Example | Your Data | Unit | Comment
Motor Power Rating | : | 45 |  | [kW] | Rated Power of Motor
Motor Efficiency | : | 93.7% |  | [%] | Efficiency of Motor (45 kW EFF1 2-pole motor efficiecy = 93.7%)
Annual Operation Hours | : | 8760 |  | [h] | 24h/7d = 8,760 hours; 24h/5d = 6,240 hours; 8h/5d = 2,080 hours.
% Switch off Time | : | 8% |  | [%] | = Amount of time switched off expressed as a % of annual operation hours
Annual Energy Use before Switch Off | : | 420704.3757 | #DIV/0! | [kWh/y] | = (Motor Power [kW]) / (Motor Efficiency [%]) x (Annual Operation Hours [h])
Annual Energy Use after Switch Off | : | 387048.0256 | #DIV/0! | [kWh/y] | = (Motor Power Rating [W]) / (Motor Efficiency [%]) x (Annual Operation Hours [h]) x ( 1- % Switch Off Time [%])
Annual Energy Savings | : | 33656.3501 | #DIV/0! | [kWh/y] | = (Annual Energy Use Before Switch Off [kWh]) - (Annual Energy Use After Switch Off [kWh])
Average Electricity Price | : | 0.14 |  | [€/kWh] | Insert from Energy Bills Analysis Tool
Annual Cost Savings | : | 4711.889 | #DIV/0! | [€/y] | =(Annual Energy Savings [kWh/y]) x (Average Electricity Price [€/kWh])
Additional Information & Tips
A common concern is that the frequent starting of motors can result in higher electricity consumption. Starting a motor does draw more power than when operating at full load because the inrush current can be between 4 and 8 times full-load current. However, because the power factor is low when starting, the power consumed is not equivalent to 4-8 times full load power. Starting usually takes under 2 seconds and rarely lasts more than 10 seconds. One additional minute of operating time after a start-up consumes far more energy than a motor start-up itself.
Another common concern relates to the maximum demand and excess MIC charges levied by electricity suppliers. The excess demand during motor start-up is of very short duration (from a couple of seconds to about 10s for larger star-delta connected motors). Therefore, it is relatively easy to stagger startups to avoid the effects of initial inrush current.
Start-ups can stress a motor by: - Applying torque loading in excess of full load; - Applying high magnetic forces to the motor windings; - Heating the rotor and stator windings. Frequent shock loading to shafts from starting could reduce system life through metal fatigue. However, most shaft failures are attributed to other mechanisms such as bearing failures, excessive belt tension and misapplication.
Although frequent stopping and starting does stress motors there is no known relationship between number of rotor starts and normal life expectancy. So unless the frequency of starting and stopping is excessive, motor life should not be significantly affected.
Source: US Department of Energy Industrial Technologies Programme Energy Tips - Motor Turn Off Motors When Not In Use 2007

## Energy-Efficient Motors
Motors - Energy-Efficient Motors
The efficiency of a motor is the ratio of mechanical power output to the electrical power input and is typically expressed as a percentage. An energy-efficient motor is simply a motor that uses less energy than a conventional one. It will deliver the same mechanical power output but requires less electrical input power. Energy-efficient motors are manufactured with higher quality materials and techniques, and therefore usually have longer bearing lives, less waste heat output, and less vibration, all of which can increase their reliability and longevity. In general, you should consider investing in an energy-efficient motor whenever you are purchasing a new or a replacement motor or thinking about repairing an existing motor. Choosing an energy-efficient motor makes sense in the following circumstances: - When purchasing new equipment packages or machines that have integrated electric motors; - When purchasing spare motors or replacing faulty motors; - As an alternative to rewinding old standard-efficiency motors; - To replace oversized and under loaded motors.
Estimate Your Savings
What Does this Sheet Do? Calculates the energy savings achievable by changing from a standard efficiency motor (EFF3) to an energy-efficient motor (EFF1)
Parameter |  | Example | Your Data | Unit | Comment
Motor Power | : | 5.5 |  | [kW] | Rated Power of Motor
Efficiency of Existing EFF3 Motor | : | 84.7% |  | [%] | Efficiency of Existing Motor
Efficiency of New High Efficiency EFF1 Motor | : | 88.6% |  | [%] | Efficiency of New Energy-efficient motor
% Full Load Loading | : | 65% |  | [%] | % of Full Load Capacity at which motor operates
Annual Operation Hours | : | 8760 |  | [h] | 24h/7d = 8,760 hours; 24h/5d = 6,240 hours; 8h/5d = 2,080 hours.
Existing Motor Electricity Usage | : | 36974.026 | #DIV/0! | [kWh/y] | = (Motor Power [kW] / Efficiency of Exisitng Motor [%]) x (% Full Load [%]) x (Annual Operation Hours [h])
Proposed Motor Electricity Usage | : | 35346.5011 | #DIV/0! | [kWh/y] | = (Motor Power [kW] / Efficiency of New Motor [%]) x (% Full Load [%]) x (Annual Operation Hours [h])
Annual Energy Savings | : | 1627.5248 | #DIV/0! | [kWh/y] | Existing MotorElectricity Usage [kWh] - Proposed Motor Electricity Usage [kWh]
Average Electricity Price | : | 0.14 |  | [€/kWh] | Insert from Energy Bills Analysis Tool
Annual Cost Savings | : | 227.8535 | #DIV/0! | [€/y] | = (Annual Energy Savings [kWh/y]) x (Average Electricity Price [€/kWh])
Payback: The capital cost of an energy-efficient motor can be 20-30% higher than that of a standard-efficiency motor. However, the running costs of a motor are a multiple of the capital cost, and an energy-efficient motor saves money during its entire lifetime. The payback period for an energy-efficient motor will depend on how much it’s used, on the size of the motor load and on the price of electricity. The simple payback of a continuously operated energy-efficient motor can be recovered through energy savings typically in less than 2 years.
Additional Information & Tips
Normally, standard-efficiency motors can be replaced directly with energy efficient motors. AC induction motors are a commodity product and most are produced in standardised frame sizes, making them interchangeable between manufacturers and between efficiency classes. However, European and US standard sizes differ. The nameplate of your existing motor will list all important design characteristics that need to be taken into account when replacing it. You should consult with your supplier of energy-efficient motors to help identify the correct replacement for an existing standard-efficiency motor.
There are several standards and classifications which are used by motor manufacturers to categorise their products as “energy-efficient”. The one most commonly referenced in Ireland is the European CEMEP classification. CEMEP (European Committee of Manufacturers of Electrical Machines and Power Electronics) defines three efficiency classes: EFF1, EFF2 and EFF3, with EFF1 being the highest efficiency classification.
Maximum full load motor efficiencies for different motor efficiency classes (EFF1 etc.) vary with motor size (kW) and number of poles. Maximum efficiency typically increases with motor size and number of poles. In the example above, an efficiency of 88.6% was assumed for a new 5.5 kW EFF1 2-pole motor. The corresponding efficiency for a 400 kW EFF1 4-pole would be 96%.
Motor sizing: Size motors to run mainly in the 65% to 100% load range. Consider replacing motors running at less than 40% load with properly sized motors. Applications with occasional high peak loads can be served using VSDs for pumps and fans, reservoirs for fluids, and fly wheels for mechanical equipment.
Motor speed: The average speed of an energy-efficient motor can be slightly higher than the average speed of an equivalent-sized standard-efficiency motor. Installing a new motor with a higher speed can result in reduced energy savings. For centrifugal pump or fan applications in particular, it is important to select a replacement motor that has a comparable full-load speed. It is also important to replace induction motors with induction motors and other types with their corrsponding equivalent. Seek specialist advice if you want to change motor types.
Inrush current: Overloading of circuits should be avoided. Energy-efficient motors will typically have a lower electrical resistance than a standard-efficiency motor, with the result that inrush currents will be higher. The duration of the inrush current is too short to trip thermal protection devices but could result in nuisance trips of in-built magnetic circuit protectors in some energy-efficient motors on start-up. The motor control and protection systems may need to be adjusted to match the new motor.

## Cogged & Synchronous Belts
Motors - Switching to Cogged or Synchronous Belts
Most belt drives use V-belts, which have a trapezoidal cross section to create wedging action on the pulleys. This increases friction and the belt's power transfer capability. A typical peak efficiency for a V-belt drives is 95% - 98% (at installation). Unfortunately, this efficiency can deteriorate by as much as 5% over time if slippage occurs because the belt is not periodically re-tensioned. Cogged belts have slots that run perpendicular to the belt. Cogged belts can be used with the same pulleys as equivalently rated V-belts. They run cooler, last longer, and can give a 2% efficiency gain (compared to standard V-belts). Synchronous belts are toothed and operate with mating toothed-drive sprockets. A typical peak efficiency for a synchronous belt is 98%. This efficiency can be maintained over a wide load range, unlike V-belt efficiency which reduces sharply at high torque.
Estimate Your Savings
What Does this Sheet Do? Calculates the energy savings achievable by changing from a V-belt to a cogged belt.
Rule of Thumb: Changing from a V-belt drive to a cogged, timing belt type drive can reduce motor energy consumption by 2% to 5%.
Parameter |  | Example | Your Data | Unit | Comment
Rated Motor Power | : | 50 |  | [kW] | Rated Power of Motor
Motor Efficiency | : | 93% |  | [%] | Efficiency of Motor
% Full Load Loading | : | 75% |  | [%] | % of Full Load Capacity at which motor operates
Efficiency gain for using a Cogged Belt | : | 2% |  | [%] | Gain in Efficiency from using a Cogged Belt (assume = 2%)
Annual Operation Hours | : | 4000 |  | [kWh/y] | 24h/7d = 8,760 hours; 24h/5d = 6,240 hours; 8h/5d = 2,080 hours.
Annual Energy Savings | : | 3225.8065 | #DIV/0! | [kWh] | (Rated Motor Power [kW]) x (% Full Loading [%]) x (Annual Operating Hours [h]) x (1/Motor Efficiency [%]) x (Efficiency Gain for Using a Cogged Belt [%])
Average Electricity Price | : | 0.14 |  | [€/kWh] | Insert from Energy Bills Analysis Tool
Annual Cost Savings | : | 451.6129 | #DIV/0! | [€/y] | = (Annual Energy Savings [kWh/y]) x (Average Electricity Price [€/kWh])
Additional Information & Tips
Cogged belt systems tend to be noisier than V-belt systems. They are also more prone to dust and other contaminants.
Synchronous belts are the most efficient choice. They require less maintenance and retensioning, operate in wet and oily environments, and run slip-free. Like cogged belts they are noiser than V-belts. They are also unsuitable for shock loads and they transfer vibrations. In these circumstances, cogged belts may be better.

## Repair or Replace
Motors - Repair or Replace
In most cases repairing or rewinding a motor reduces its efficiency by about 1 or 2%, depending on the motor size. Couple this with the efficiency difference between an existing EFF3 motor and a new high efficiency EFF1 replacement motor, and a new motor will be typically 3-5% more efficient than an existing one. Taking these efficiency differences into account will mean that increased running costs will quickly exceed the initial savings from rewinding a motor instead of replacing it. Therefore when considering whether to repair or replace a motor the choice should not just depend on the purchase cost of a new motor versus the repair cost of the old motor, but also the running costs associated with the operation of the motor during its lifetime.
Estimate Your Savings
What Does this Sheet Do? Calculates the energy savings achievable by changing from a repaired (rewound) EFF3 motor to a new high efficiency (EFF1) motor.
Rule of Thumb: The efficiency difference between a new high efficiency motor and an existing rewound motor will typically be the difference in the nameplate efficiencies plus 1 or 2% depending on the motor size, although rewinding efficiencies can vary dramatically depending on the materials used and the techniques applied.
Parameter |  | Example | Your Data | Unit | Comment
Existing Motor Power | : | 5.5 |  | [kW] | Rated Power of Existing Motor
Existing EFF3 Motor Efficiency After Rewind | : | 82.7% |  | [%] | Efficiency of existing motor, taking account of rewinding losses and lower efficiency to begin with (use 84.7% - 2% rewinding losses for 5.5 kW EFF3 motor)
New EFF1 Motor Efficiency | : | 88.6% |  | [%] | Efficiency of new EFF1 Motor
% Full Load Loading | : | 85% |  | [%] | % of Full Load Capacity at which motor operates
Annual Operation Hours | : | 8760 |  | [h/y] | 24h/7d = 8,760 hours; 24h/5d = 6,240 hours; 8h/5d = 2,080 hours.
Annual Energy Use - Existing Motor | : | 49519.9516 | #DIV/0! | [kWh/y] | = (Motor Power [kW]) / (Existing Motor Efficiency [%]) x (Annual Operation Hours [h]) x (% Full Load Loading [%])
Annual Energy Use - New Motor | : | 46222.3476 | #DIV/0! | [kWh/y] | = (Motor Power [kW]) / (New Motor Efficiency [%]) x (Annual Operation Hours [h]) x (% Full Load Loading [%])
Annual Energy Savings | : | 3297.604 | #DIV/0! | [kWh/y] | = (Annual Energy Use Old Motor [kWh]) - (Annual Energy Use New Motor [kWh])
Average Electricity Price | : | 0.14 |  | [€/kWh] | Insert from Energy Bills Analysis Tool
Annual Cost Savings | : | 6932.7932 | #DIV/0! | [€/y] | = (Annual Energy Savings [kWh/y]) x (Average Electricity Price [€/kWh])
Payback: In order to calculate the payback associated with replacing a motor you should take into account the cost of rewinding the existing motor, the cost of a new high efficiency motor, the associated savings with a high efficiency motor and the operational lifetime of the motors.
Additional Information & Tips
Maximum full load motor efficiencies for different motor efficiency classes (EFF1 etc.) vary with motor size (kW) and number of poles. Maximum efficiency typically increases with motor size and number of poles. In the example above, an efficiency of 88.6% was assumed for a new 5.5 kW EFF1 2-pole motor. The corresponding efficiency for a 400 kW EFF1 4-pole would be 96%.
If you are considering rewinding a motor it would be advisable to contact a reputable motor rewinding company and ask them for an estimate of the rewinding efficiency losses specific to your motor.
Generally it is advised to replace an existing motor with a new high efficiency motor if the cost of a rewind exceeds 60% of the cost of a new motor. It is almost always best practice to replace motors smaller than 11kW
Source: UK Carbon Trust Motors Technology Overview 2007, US Department of Energy Industrial Technologies Programme Determining Electric Motor Load and Efficiency

## ACA
Accelerated Capital Allowance (ACA)
In addition to saving money by operating more energy efficient equipment, companies that pay corporation tax can improve cashflow by investing in equipment that qualifies for the Accelerated Capital Allowance (ACA) scheme operated by SEAI. This is a tax incentive for companies to purchase energy efficient equipment. To see which equipment qualifies for ACA and to find out more go to www.seai.ie/aca or click on the graphic below. There is also useful technical information available on the qualifying equipment.
Estimate Your Savings
What Does this Sheet Do? Calculates the Cashflow savings achievable by availing of Accelerated Capital Allowances for qualifying energy-efficient equipment.
Rule of Thumb: ACA allows companies to write off 100% of the purchase value of specified energy efficient equipment in the year of purchase.
Parameter |  | Example | Your Data | Unit | Comment
Capital cost of Qualifying Equipment | : | 100000 |  | [€] | See www.seai.ie/aca for details of qualifying equipment | 1562.5 | 0
Corporation Tax Rate | : | 12.5% | 12.5% | [%] |  | 1562.5 | 0
Actual Year 1 Net Cashflow without ACA | : | 98437.5 | 0 | [€] | Standard capital allowance allows firms to write off 1/8 of capital cost against tax each year (for 8 years) | 1562.5 | 0
Actual Year 1 Net Cashflow with ACA | : | 87500 | 0 | [€] | Accelerated capital allowance allows firms to write off ALL of capital cost against tax in first year | 1562.5 | 0
Year 1 Saving in Net Cashflow | : | 10937.5 | 0 | [€] | = (Actual Year 1 Net Cashflow without ACA) - (Actual Year 1 Net Cashflow with ACA) | 1562.5 | 0
Discount Rate | : | 9% |  | [%] | The Discount Rate used by your business | 1562.5 | 0
PV of standard Capital Allowance |  | 9426.4888 | 0 | [€] | Present Value (PV) to your business of the Standard Capital Allowances, i.e. no ACA | 1562.5 | 0
PV of Accelerated Capital Allowance |  | 12500 | 0 | [€] | Present Value (PV) to your business of the Accelerated Capital Allowances, i.e. with ACA | 1562.5 | 0
Additional Information & Tips
With the standard capital allowance for plant and machinery, the tax saving is spread equally over eight years and therefore also subject to typical monetary devaluation. With the ACA, it is all recovered in the first year, resulting in direct cash flow benefits without degradation of value with time.
In summary, the ACA benefits you by ensuring: - increased opportunities for further investment - a shorter break-even period on the investment - a higher return on the investment - lower ongoing energy costs through using energy-efficient equipment - a marketing edge through being environmentally friendly - a higher real value on capital allowance return in an inflationary market
Remember that these savings are in addition to the operational savings (energy, € and environmental) associated with using energy efficient equipment.
Source: www.seai.ie/aca

## Version
Energy MAP Tool Version History
Version | Description of Modification(s) | Date | Additional Comments
Draft | Issued to SEI for review | 2009-12-23
1 | Final - for publication | 2009-06-09
2 | Final - updated logos and links to reflect SEAI rebranding | 2010-10-05
3 | Addition of Intro Sheet Edits for PS organisations | 2012-09-06 | 2012 Review of Energy MAP 'Family' Issued for internal review
4 | Additional guidance text | 2012-10-16 | Issued for publication on SEAI website