## Intro
Energy MAP
Best Practice Worksheet - Pumps
Version 4
This Best Practice Worksheet for Pumps is for identifying and quantifying energy savings opportunities associated with the operation of pumps.
Your organisation should continuously identify opportunities for energy savings and record them in the Register of Opportunities. There should be a clear link between the opportunities and the Significant Energy Users in your organisation, e.g. pumps.
Layout of this Tool
- Green worksheets: this is where you enter data
- Blue worksheets: summary or example data
- Red worksheets: For SEAI use only
Using this Tool
- | Enter data in the green cells only
- | Each worksheet contains information, tips and calculation methods and examples for a different savings opportunity
Additional Information & Support
- There is extensive guidance on all twenty Energy MAP steps at www.seai.ie/energymap (click here)
- Click here to see SEAI's suite of supports to help public bodies reach their 33% energy-efficiency targets by 2020
- Click here to see SEAI's supports for SMEs and Large Industry

## ReadMe
The "Onion" Approach to Improving Energy Efficiency
1 | Start at the centre of the Onion (see diagram below) by identifying the relevant Energy Service. An energy service demand is the need for a specific level of work or activity to be performed. However, an Energy Service is more than simply 'pumping'. To identify the Energy Service, ask yourself: - What do I want to do with the pumped fluid? - What is the fundamental piece of work that I want the pump to do? An example of a pump related Energy Service might be: to transport feedwater from a tank to a boiler.
2 | Then, for each Energy Service, ask yourself: - Do I really need (paid-for) energy to deliver this energy service? - Is there another way of delivering the output that requires using less or no energy? - Can I use a less energy intensive alternative? - What is the minimum specification required? - Can I reduce (increase) pressures, temperatures, run times, flowrates, currents etc. to reduce the energy required?
3 | Start at the point of energy service demand and work back upstream through the energy distribution and conversion system(s) – this is consistent with the energy efficiency hierarchy.
4 | Is the technology that is currently satisfying each energy service demand appropriate? Or can it be eliminated or replaced by a more effective alternative?
5 | Can the system be designed better?
6 | Identify the most efficient / optimum operational control parameters for the most effective technology to satisfy each service demand. Can cycle times be adjusted?
7 | Are there opportunities to distribute the energy more efficiently, e.g. insulation, improved structural integrity (elimination of leaks), isolation etc.?
8 | Is there scope for technical or operational modifications to the energy conversion systems (compressors, boilers, chillers etc.) to reduce the consumption of energy resources (natural gas, gasoil, electricity, wood chips etc.)?
9 | Finally, are there O&M or housekeeping actions that can be taken to reduce the consumption of energy resources?
10 | The following Onion diagram illustrates this approach and also identifies some best practice energy savings measures at different 'layers'. Simple energy saving calculation sheets for each of these measures are included in this spreadsheet.
11 | The Triple E Products Register is a new benchmark register of best in class energy efficient products. Products on this register all meet a minimum set of stringent efficiency criteria and typically will be of a best in class efficiency standard. As such, procuring against this register will provide you with the assurance that you are purchasing a product of very high efficiency. For more information go to www.seai.ie/triplee. Public bodies are obliged to only procure equipment or vehicles that are listed on the register (or equivalent).
12 | SEAI operates an accelerated capital allowance (ACA) scheme, which is a tax incentive for companies that pay corporation tax to purchase energy efficient equipment. It allows companies to write off 100% of the purchase value of specified energy efficient equipment in the year of purchase. To see which equipment qualifies for ACA and to find out more go to www.seai.ie/aca or click on the graphic below. There is also useful technical information available on the qualifying equipment. There is also an ACA worksheet in this spreadsheet.

## Trim Impeller (Throttle)
Pumps - Trim Impeller (Throttle Control)
Pumps can often be substantially larger than they need to be when in use in industrial systems. Pumps are often oversized because of rounding up, trying to accommodate gradual increases in pipe surface roughness and due to anticipating future system capacity increases. As a result of this, oversized pumps can have operating points different to their design points. This can result in cavitation and energy wastage because some other means of control (e.g. throttle or bypass valves) have to be used to regulate the system flow.
In systems where the flow is constantly throttled to some degree, the pump is not operating at peak efficiency and energy savings can be made by using a smaller impeller to generate similar flow at a lower head (while opening the throttling valve) and thereby demanding less power. Some suppliers manufacture a range of impellers and a smaller one may be easily sourced. In other situations, the user may need to trim the impeller. Impeller trimming involves machining the impeller to a smaller diameter and then refitting it to the pump. Where the pump is in near continuous use and downtime has to be kept to a minimum often a smaller impeller can be ordered rather than waiting while the existing impeller is machined. Downsizing the impeller has the effect of reducing both the flow rate and the pressure at which the pump operates. As a result the pump uses less energy during its operation. Care should be taken when trimming an impeller as excessive trimming can result in added clearance between the impeller and the impeller casing and this can cause internal flow recirculation, head loss and a reduction in pump efficiency. Typically an impeller should not be resized to less than 75% of its original size.
Estimate Your Savings
What Does this Sheet Do? This sheet calculates the energy saving achieved by reducing pump impeller size and removing the system head due to throttle valve control.
Rule of Thumb: A first-cut estimate of the energy used in throttled systems can be approximated by the formula [{0.38 x Rated Power} + {0.62 x Rated Power x (% Flow Rate)^0.7}]. A first-cut estimate of the power used in the trimmed impeller system is given by (Rated Power) x (% Flow Rate)^2. This formula allows for the presence of static head.
Parameter |  | Example: Load Condition 1 | Example: Load Condition 2 | Example: Load Condition 3 | Your Data: Load Condition 1 | Your Data: Load Condition 2 | Your Data: Load Condition 3 | Unit | Comment
Pump Motor Power | : | 74.6 | 74.6 | 74.6 |  |  |  | [kW] | Rated Power of Pump Motor
Pump Motor Efficiency | : | 90% | 90% | 90% |  |  |  | [%] | Efficiency of Pump Motor
New Impeller: % Max Flow wrt Max Flow of Old Impeller | : | 75% | 75% | 75% |  |  |  | [%] | New Flow Rate wrt Maximum Flow Rate [%] (Hint: Equal to New Impeller Diameter / Old Impeller Diameter [%])
New Impeller Maximum Power | : | 41.9625 | 41.9625 | 41.9625 | 0 | 0 | 0 | [kW] | =(Old Rated power) x (% Flow Rate [%])2
% Load Profile | : | 40% | 60% | 80% |  |  |  | [%] | Load Profile wrt Maximum Flow (Hint: Match the operating hours (row 16) to the (up to) three Load Conditions on this row)
Annual Operation Hours | : | 1000 | 1000 | 1000 |  |  |  | [h] | Operating Hours at each % load (load condition)
Power Consumed (Throttled Pump & Old Impeller) | : | 58.5579 | 67.4391 | 75.4571 | #DIV/0! | #DIV/0! | #DIV/0! | [kW] | =((0.38 x Motor Rating [kW]) + (0.62 x Motor Rating [kW]) x (% Flow Rate [%]0.7)) / (Motor Efficiency [%])
Power Consumed (New Impeller) | : | 32.9388 | 37.9345 | 42.4446 | #DIV/0! | #DIV/0! | #DIV/0! | [kW] | =(0.38 x Motor Rating [kW]) + (0.62 x Motor Rating [kW]) x (% Flow Rate [%]0.7) / (Motor Efficiency [%])
Power Savings | : | 25.6191 | 29.5046 | 33.0125 | #DIV/0! | #DIV/0! | #DIV/0! | [kW] | = (Power With Throttled Pump and old impeller [kW]) - (Power with New Impeller [kW])
Annual Energy Savings at Each Flow Condition | : | 25619.088 | 29504.6002 | 33012.4817 | #DIV/0! | #DIV/0! | #DIV/0! | [kWh/y] | = (Power Savings [kW]) x (Annual Operating Hours [h])
Average Electricity Price | : | 0.14 | 0.14 | 0.14 |  | 0 | 0 | [€/kWh] | Insert from Energy Bills Analysis Tool
Annual Cost Savings at Each Flow Condition | : | 3586.6723 | 4130.644 | 4621.7474 | #DIV/0! | #DIV/0! | #DIV/0! | [€/y] | = (Annual Energy Savings at Each Flow Condition [kWh/y]) x (Average Electricity Price [€/kWh])
Total Annual Cost Saving | : |  |  | 12339.0638 |  |  | #DIV/0! | [€/y] | = Sum of the Annual Cost Savings for the 3 Flow Conditions
Payback: The payback will depend on the cost to replace the impeller, the initial load profile and the amount of hours the pump is in operation at the various load profile.
Additional Information & Tips
Due to standardisation pump casings and shafts are designed to accommodate impellers of different sizes. Many pump manufacturers provide pump performance curves indicating how various models will perform with pump impellers of different diameters. An estimate of ther performance of the trimmed impeller can be made by using interpolation on the pump curves for different impeller sizes. Impeller trimming has an effect similar to reducing the pump size, so it may be considered a more cost effective solution than buying a smaller pump, depending on the circumstances. It is also worth noting that replacing an impeller with a smaller impeller will incur more cost than trimming an impeller on a lathe. Impeller trimming should only be undertaken by suitably qualified individuals under the guidance of pump experts.
Source: UK Carbon Trust Energy Savings in Industrial Water Pumping Systems 1997, U.S Department of Energy Industrial Technologies Programme Energy Tips - Pumping Systems 2007, US Best Practice Sheets

## Trim Impeller (Bypass)
Pumps - Trim Impeller
Pumps can often be substantially larger than they need to be when in use in industrial systems. Pumps are often oversized because of rounding up, trying to accommodate gradual increases in pipe surface roughness and due to anticipating future system capacity increases. As a result of this, oversized pumps can have operating points different to their design points. This can result in cavitation and energy wastage because some other means of control (e.g. throttle or bypass valves) have to be used to regulate the system flow.
In systems where bypass control is used to regulate the system flow the system pump is operating constantly at an output that exceeds the system demand with the excess flow being returned to the pump. By reducing the impeller size you can effectively reduce the flow and head generated across the pump to a level that more closely matches the system requirements. Impeller trimming involves machining the impeller to a smaller diameter and then refitting it to the pump. Where the pump is in near continuous use and downtime has to be kept to a minimum often a smaller impeller can be ordered rather than waiting while the existing impeller is machined. Downsizing the impeller has the effect of reducing both the flow rate and the pressure at which the pump operates. As a result the pump uses less energy during its operation. Care should be taken when trimming an impeller as excessive trimming can result in added clearance between the impeller and the impeller casing and this can cause internal flow recirculation, head loss and a reduction in pump efficiency. Typically an impeller should not be resized to less than 75% of its original size.
Estimate Your Savings
What Does this Sheet Do? This sheet calculates the energy saving achieved by reducing pump impeller size in a bypass control system.
Rule of Thumb: For systems using bypass control the power used is approximately 100% of the Rated Power divided by the efficiency, for all system flow conditions. A first-cut estimate of the power used in the trimmed impeller system is given by (Rated Power) x (% Flow Rate)^2. This formula allows for the presence of static head.
Parameter |  | Example: | Your Data: | Unit | Comment
Pump Motor Power | : | 20 |  | [kW] | Rated Power of Pump Motor
Pump Motor Efficiency | : | 90% |  | [%] | Efficiency of Pump Motor
New Impeller: % Max Flow wrt Max Flow of Old Impeller | : | 75% |  | [%] | New Flow Rate wrt Maximum Flow Rate [%] (Hint: Equal to New Impeller Diameter / Old Impeller Diameter [%])
Annual Operation Hours | : | 4000 |  | [h] | Operating Hours
Power Consumed (Bypass Control & Old Impeller) | : | 22.2222 | #DIV/0! | [kW] | =Pump Motor Power [kW] / (Motor Efficiency [%])
Power Consumed (New Impeller) | : | 12.5 | #DIV/0! | [kW] | = ((Rated power [kW]) x (% Flow Rate [%] )2 ) / Motor Efficiency [%]
Power Savings | : | 9.7222 | #DIV/0! | [kW] | = (Power with bypass control & old impeller [kW]) - (Power with New Impeller [kW])
Annual Energy Savings at Each Flow Condition | : | 38888.8889 | #DIV/0! | [kWh/y] | = (Power Savings [kW]) x (Annual Operating Hours [h])
Average Electricity Price | : | 0.14 |  | [€/kWh] | Insert from Energy Bills Analysis Tool
Annual Cost Savings at Each Flow Condition | : | 5444.4444 | #DIV/0! | [€/y] | = (Annual Energy Savings at Each Flow Condition [kWh/y]) x (Average Electricity Price [€/kWh])
Payback: The payback will depend on the cost to replace the impeller, the initial load profile and the amount of hours the pump is in operation at the various load profile.
Additional Information & Tips
Due to standardisation pump casings and shafts are designed to accommodate impellers of different sizes. Many pump manufacturers provide pump performance curves indicating how various models will perform with pump impellers of different diameters. Impeller trimming has an effect similar to reducing the pump size, so it may be considered a more cost effective solution than buying a smaller pump, depending on the circumstances. It is also worth noting that replacing an impeller with a smaller impeller will incur more cost than trimming an impeller on a lathe. Impeller trimming should only be undertaken by suitably qualified individuals under the guidance of pump experts.
Source: UK Carbon Trust Energy Savings in Industrial Water Pumping Systems 1997, U.S Department of Energy Industrial Technologies Programme Energy Tips - Pumping Systems 2007, US Best Practice Sheets

## Bypass to VSD
Pumps - Bypass Control to VSD Control
A Variable Speed Drive (VSD) is a device that controls the rotational speed of motor driven equipment. It does this by adjusting the frequency and voltage of the power supplied to an AC motor according to system requirements. These inputs can be controlled manually, although in most applications an automatic control loop is used. In a closed control loop a transducer monitors the flow-rate or pressure and then a process controller generates the correct speed-demand response automatically. This method of control has the advantage of creating a quick response time to system changes and helps to maximise savings.
Where a motor is operating under light loading conditions the addition of a VSD can result in energy savings. The VSD saves energy by matching the motor output to the part load condition. The magnitude of these savings depends on the Torque-Speed characteristics of the load being driven. There are three types of relationships: Varying Torque, Constant Torque and Constant Power. In systems where the load characteristic is that of Varying Torque the power used by the motor is proportional to the cube of the motor speed in accordance with the Affinity Laws. As a result, a 20% reduction in motor speed corresponds to a reduction of over 50% in power consumed. However, as most real systems have some component of static head the relationship must be altered to account for this. Despite this, systems with static head losses of less than 20% offer cost effective opportunities for savings. Variable Torque Loads include Fans and Centrifugal Pumps. Typical efficiency for VSDs is in the range of 92-95% with the 5-8% losses occurring as heat dissipation due to electrical switching within the controls.
Important Note: Positive displacement pumps are of a Constant Torque load characteristic and may not realise the same amount of energy savings from a speed reduction.
Estimate Your Savings
What Does this Sheet Do?: Calculates the energy saving achieved by fitting a VSD to a system previously controlled using a bypass valve.
Rule of Thumb: The energy used in bypass systems can be calculated as (Rated Motor Capacity / % Motor Efficiency) as the pump is under constant operation. A first-cut estimate of the energy used in VSD systems can be approximated by (Rated Power) x (% Flow Rate)^2. This includes the impact of a static head pressure.
Parameter |  | Example: Load Condition 1 | Example: Load Condition 2 | Example: Load Condition 3 | Your Data: Load Condition 1 | Your Data: Load Condition 2 | Your Data: Load Condition 3 | Unit | Comment
Pump Motor Power | : | 40 | 40 | 40 |  |  |  | [kW] | Rated Power of Pump Motor
Motor Efficiency Rating at Design Output | : | 90% | 98% | 98% |  |  |  | [%] | Efficiency of Pump Motor at Design Flow
Variable Speed Drive Efficiency Rating | : | 98% | 100% | 100% |  |  |  | [%] | VSD Efficiency Rating
% Load Profile | : | 25% | 50% | 100% |  |  |  | [%] | Load Profile wrt Maximum Flow (Hint: Match the operating hours (row 19) to the (up to) three Load Conditions on this row)
Hours of Operation at Each Flow Rate | : | 1000 | 4000 | 1000 |  |  |  | [h] | Operating Hours at each % load (load condition)
Power Used With Bypass System | : | 44.4444 | 40.8163 | 40.8163 | #DIV/0! | #DIV/0! | #DIV/0! | [kW] | = Rated Power [kW] / Motor Efficiency [%]
Power Used With Variable Speed Pump | : | 2.8345 | 10.2041 | 40.8163 | #DIV/0! | #DIV/0! | #DIV/0! | [kW] | = ((Rated power [kW]) x (% Flow Rate [%] )2 / (VSD Efficiency [%])) / Motor Efficiency [%]
Power Savings | : | 41.61 | 30.6122 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | [kW] | = Power with Bypass System [kW] - Power Used with Variable Speed Pump [kW]
Annual Energy Savings at Each Flow Condition | : | 41609.9773 | 122448.9796 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | [kWh] | = Power Savings [kW] x Hours of Operation at Each Flow Rate [h]
Average Electricity Price | : | 0.14 | 0.14 | 0.14 |  | 0 | 0 | [€/kWh] | Insert from Energy Bills Analysis Tool
Annual Cost Savings at Each Flow Condition | : | 5825.3968 | 17142.8571 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | [kWh/y] | = (Annual Energy Savings at Each Flow Condition [kWh/yr]) x (Average Electricity Price [€/kWh])
Total Annual Cost Savings | : |  |  | 22968.254 |  |  | #DIV/0! | [€/y] | = Sum of the Annual Cost Savings for the 3 Flow Conditions
Payback: In order to evaluate the payback for a VSD the system most be monitored for a period of time to evaluate a duty load cycle. While VSDs are relatively expensive, typical payback periods can be as low as less than two years depending on the cost of the system and the savings to be made due to the part loading of the system. Bypass controlled systems will have shorter payback periods than throttled controlled systems due to their constant operation at full load.
Additional Information & Tips
Before deciding to install a VSD ensure the system is as efficient as possible. It is then advisable to monitor the existing equipment for a period of time to identify if the system motor is running at a capacity lower than design capacity. Doing so ensures that a VSD is actually required, that it can be sized correctly, and maximum savings can be made. As outlined above, the most suitable systems for installation of a VSD are those where the motor output is not 100% utilised, however before coming to the conclusion that a VSD is required you should consider motor resizing. For example, if a system is only working at a maximum of 40% of motor output it might be more advantageous to resize the motor to that of half of the original size. Now the new motor is operating up to 80% of its maximum output and the addition of a VSD might not incur any further savings.
When calculating the energy savings with a VSD it is important to consider the the efficiency of the VSD and also the efficiency of the motor when it is operating partially loaded and at a reduced speed to satisfy system requirements. The motor manufacturer should be consulted if it is planned to use a VSD to significantly reduce the speed of the motor as this will reduce the cooling effect of the motor fan. It may be prudent to set a minimum speed on the VSD to prevent overheating of the motor especially in high temperature summer conditions.
Source: UK Carbon Trust Variable Speed Drive CTG006 2007; Energy Savings in Industrial Water Pumping Systems 1997, U.S Department of Energy Industrial Technologies Programme Energy Tips - Motor 2007, US Best Practise Sheets

## Throttle to VSD
Pumps - Throttled Control to VSD Control
A Variable Speed Drive (VSD) is a device that controls the rotational speed of motor driven equipment. It does this by adjusting the frequency and voltage of the power supplied to an AC motor according to system requirements. These inputs can be controlled manually, although in most applications an automatic control loop is used. In a closed control loop a transducer monitors the flow-rate or pressure and then a process controller generates the correct speed-demand response automatically. This method of control has the advantage of creating a quick response time to system changes and helps to maximise savings.
Where a motor is operating under light loading conditions the addition of a VSD can result in energy savings. The VSD saves energy by matching the motor output to the part load condition. The magnitude of these savings depends on the Torque-Speed characteristics of the load being driven. There are three types of relationships: Varying Torque, Constant Torque and Constant Power. In systems where the load characteristic is that of Varying Torque the power used by the motor is proportional to the cube of the motor speed in accordance with the Affinity Laws. As a result, a 20% reduction in motor speed corresponds to a reduction of over 50% in power consumed. However, as most real systems have some component of static head the relationship must be altered to account for this. Despite this, systems with static head losses of less than 20% offer cost effective opportunities for savings. Variable Torque Loads include Fans and Centrifugal Pumps. Typical efficiency for VSDs is in the range of 92-95% with the 5-8% losses occurring as heat dissipation due to electrical switching within the controls.
Important Note: Positive displacement pumps are of a Constant Torque load characteristic and may not realise the same amount of energy savings from a speed reduction.
Estimate Your Savings
What Does this Sheet Do?: Calculates the energy saving achieved by fitting A VSD to a system previusly controlled using a throttled valve.
Rule of Thumb: The following formula provides an estimate of the energy used in throttled systems [{0.38 x Rated Power} + {0.62 x Rated Power x (% Flow Rate)0.7}]. The energy used in VSD systems can be approximated by (Rated Power) x (% Flow Rate)^2, this includes the impact of a static head pressure.
Parameter |  | Example: Load Condition 1 | Example: Load Condition 2 | Example: Load Condition 3 | Your Data: Load Condition 1 | Your Data: Load Condition 2 | Your Data: Load Condition 3 | Unit | Comment
Pump Motor Power | : | 30 | 30 | 30 |  |  |  | [kW] | Rated Power of Pump Motor
Pump Motor Efficiency Rating |  | 90% | 90% | 90% |  |  |  | [%] | Efficiency of Pump Motor
Variable Speed Drive Efficiency Rating |  | 98% | 98% | 98% |  |  |  | [%] | VSD Efficiency Rating
Enter Load Profile, % Rated Flow Capacity of Pump |  | 25% | 50% | 100% |  |  |  | [%] | Load Profile wrt Maximum Flow (Hint: Match the operating hours (row 20) to the (up to) three Load Conditions on this row)
Hrs/yr for Each %Flow Rate | : | 1000 | 4000 | 1000 |  |  |  | [h] | Operating Hours at each % load (load condition)
Power With Throttled Pump | : | 20.4979 | 25.3885 | 33.3333 | #DIV/0! | #DIV/0! | #DIV/0! | [kW] | ={0.38 x Connected Motor Power) + (0.62 x Connected Motor Power [kW] x (% Flow Rate [%])0.7) / Motor Efficiency [%]
Power With Variable Speed Pump | : | 2.1259 | 8.5034 | 34.0136 | #DIV/0! | #DIV/0! | #DIV/0! | [kW] | = ((Rated power [kW]) x (% Flow Rate [%] )2 / VSD Efficiency [%]) / Motor Efficiency [%]
Power Savings | : | 18.372 | 16.8851 | -0.68027 | #DIV/0! | #DIV/0! | #DIV/0! | [kW] | = Power with Throttled Pump [kW] - Power with Variable Speed Pump [kW]
Annual Energy Savings at Each Flow Condition | : | 18372.0186 | 67540.3636 | -680.2721 | #DIV/0! | #DIV/0! | #DIV/0! | [kWh] | = Power Savings [kW] x Hours of Operation at Each Flow Rate [h]
Average Electricity Price | : | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | [€/kWh] | Insert from Energy Bills Analysis Tool
Annual Cost Savings at Each Flow Condition | : | 2572.0826 | 9455.6509 | -95.2381 | #DIV/0! | #DIV/0! | #DIV/0! | [€/y] | = (Annual Energy Savings at Each Flow Condition [kWh/y]) x (Average Electricity Price [€/kWh])
Total Annual Cost Savings | : |  |  | 11932.4954 |  |  | #DIV/0! | [€/y] | = Sum of the Annual Cost Savings for the 3 Flow Conditions
Payback: In order to evaluate the payback for a VSD the system most be monitored for a period of time to evaluate a duty load cycle for the system. While VSDs are relatively expensive typical payback periods can be as low as less than two years depending on the cost of the system and the savings to be made due to the part loading of the system.
Additional Information & Tips
Before deciding to install a VSD ensure the system is as efficient as possible. It is then advisable to monitor the existing equipment for a period of time to identify if the system motor is running at a capacity lower than design capacity. Doing so ensures that a VSD is actually required, that it can be sized correctly, and maximum savings can be made. As outlined above, the most suitable systems for installation of a VSD are those where the motor output is not 100% utilised, however before coming to the conclusion that a VSD is required you should consider motor resizing. For example, if a system is only working at a maximum of 40% of motor output it might be more advantageous to resize the motor to that of half of the original size. Now the new motor is operating up to 80% of its maximum output and the addition of a VSD might not incur any further savings.
When calculating the energy savings with a VSD it is important to consider the the efficiency of the VSD and also the efficiency of the motor when it is operating partially loaded and at a reduced speed to satisfy system requirements. The motor manufacturer should be consulted if it is planned to use a VSD to significantly reduce the speed of the motor as this will reduce the cooling effect of the motor fan. It may be prudent to set a minimum speed on the VSD to prevent overheating of the motor especially in high temperature summer conditions.
Source: UK Carbon Trust Variable Speed Drive CTG006 2007; Energy Savings in Industrial Water Pumping Systems 1997, U.S Department of Energy Industrial Technologies Programme Energy Tips - Motor 2007, US Best Practise Sheets

## ACA
Accelerated Capital Allowance (ACA)
In addition to saving money by operating more energy efficient equipment, companies that pay corporation tax can improve cashflow by investing in equipment that qualifies for the Accelerated Capital Allowance (ACA) scheme operated by SEAI. This is a tax incentive for companies to purchase energy efficient equipment. To see which equipment qualifies for ACA and to find out more go to www.seai.ie/aca or click on the graphic below. There is also useful technical information available on the qualifying equipment.
Estimate Your Savings
What Does this Sheet Do? Calculates the Cashflow savings achievable by availing of Accelerated Capital Allowances for qualifying energy-efficient equipment.
Rule of Thumb: ACA allows companies to write off 100% of the purchase value of specified energy efficient equipment in the year of purchase.
Parameter |  | Example | Your Data | Unit | Comment
Capital cost of Qualifying Equipment | : | 100000 |  | [€] | See www.seai.ie/aca for details of qualifying equipment | 1562.5 | 0
Corporation Tax Rate | : | 12.5% | 12.5% | [%] |  | 1562.5 | 0
Actual Year 1 Net Cashflow without ACA | : | 98437.5 | 0 | [€] | Standard capital allowance allows firms to write off 1/8 of capital cost against tax each year (for 8 years) | 1562.5 | 0
Actual Year 1 Net Cashflow with ACA | : | 87500 | 0 | [€] | Accelerated capital allowance allows firms to write off ALL of capital cost against tax in first year | 1562.5 | 0
Year 1 Saving in Net Cashflow | : | 10937.5 | 0 | [€] | = (Actual Year 1 Net Cashflow without ACA) - (Actual Year 1 Net Cashflow with ACA) | 1562.5 | 0
Discount Rate | : | 9% |  | [%] | The Discount Rate used by your business | 1562.5 | 0
PV of standard Capital Allowance |  | 9426.4888 | 0 | [€] | Present Value (PV) to your business of the Standard Capital Allowances, i.e. no ACA | 1562.5 | 0
PV of Accelerated Capital Allowance |  | 12500 | 0 | [€] | Present Value (PV) to your business of the Accelerated Capital Allowances, i.e. with ACA | 1562.5 | 0
Additional Information & Tips
With the standard capital allowance for plant and machinery, the tax saving is spread equally over eight years and therefore also subject to typical monetary devaluation. With the ACA, it is all recovered in the first year, resulting in direct cash flow benefits without degradation of value with time.
In summary, the ACA benefits you by ensuring: - increased opportunities for further investment - a shorter break-even period on the investment - a higher return on the investment - lower ongoing energy costs through using energy-efficient equipment - a marketing edge through being environmentally friendly - a higher real value on capital allowance return in an inflationary market
Remember that these savings are in addition to the operational savings (energy, € and environmental) associated with using energy efficient equipment.
Source: www.seai.ie/aca

## Version
Energy MAP Tool Version History
Version | Description of Modification(s) | Date | Additional Comments
Draft | Issued to SEI for review | 2009-12-23
1 | Final - for publication | 2009-06-09
2 | Final - updated logos and links to reflect SEAI rebranding | 2010-10-05
3 | Addition of Intro Sheet Edits for PS organisations | 2012-09-06 | 2012 Review of Energy MAP 'Family' Issued for internal review
4 | Additional guidance text | 2012-10-16 | Issued for publication on SEAI website