GUIDANCE NOTES FOR SUBMISSIONS TO THE SUSTAINABLE ENERGY AUTHORITY OF IRELAND (SEAI) HOME-HEATING APPLIANCES REGISTER OF PERFORMANCE (HARP) DATABASE

(TWIN BURNER COOKER BOILERS ONLY)

Contents

1	Introduction

  - Twin Burner Cooker Boiler Data

  - Efficiency Data

  - Route to Product Identification

2	Help and Advice on Supplying Efficiency Data

2.1	How go I make a Submission to the Database?

2.2	Manual Entry

## Appendix 1		Manual Entry Forms

Appendix 2	Twin Burner Cooker Boiler Identity Form

Appendix 3		Route to Product Identification

Appendix 4	Notified Body Declaration Form

Appendix 5		DEAP calculations

Appendix 6	LPG Twin Burner Cooker Boiler Declaration Form

Appendix 7		Submission Check List

Appendix 8		List of Heating Products published on the HARP Database

Appendix 9		Glossary of Terms

# HOME-HEATING APPLIANCES REGISTER OF PERFORMANCE (HARP) DATABASE

- Introduction

The Sustainable Energy Authority of Ireland (SEAI) is Ireland's national energy authority with a mission to promote and assist the development of sustainable energy. This encompasses environmentally and economically sustainable production, supply and use of energy, in support of Government policy, across all sectors of the economy. Its remit relates mainly to improving energy efficiency, advancing the development and competitive deployment of renewable sources of energy and combined heat and power, and reducing the environmental impact of energy production and use, particularly in respect of greenhouse gas emissions.

One of SEAI's responsibilities is to assist the Department of Communications, Marine and Natural Resources and the Department of the Environment, Heritage and Local Government in implementing the EU Energy Performance of Buildings Directive (EPBD) [2002/91/EC] in Ireland.

Articles 4 and 5 of the EPBD require that new buildings meet minimum energy performance requirements, which in Ireland's case will be specified in the Building Regulations and Technical Guidance Document Part L.

Furthermore, Article 7 of the EPBD requires that an energy performance certificate is made available to prospective buyers or tenants when a building is constructed, sold or rented out. Throughout these Guidance Notes this requirement will be termed “building energy rating” (BER). A BER includes the label and the advisory report.

In Ireland, the approach will be to adopt not only an official national method and one official software tool that all Registered Assessors will use to carry out a BER for a dwelling.

The official national method has been developed and is entitled the “Dwelling Energy Assessment Procedure” (DEAP) and it will be used to demonstrate compliance with the Building Regulations and for preparing BERs.

1.1	TWIN BURNER COOKER BOILER DATA

The primary purpose of the Database is to support the Irish Government’s Dwelling Energy Procedure (DEAP) for energy rating of dwellings by providing reliable data on the efficiency and other relevant characteristics of domestic Twin Burner Cooker boilers.

These Guidance Notes deal specifically with the submission of data relating to gas & oil domestic Twin Burner Cooker boilers only.  Other notes exist for other domestic heating products published on the database (see Appendix 9).  These may be obtained via the website (www.seai.ie/harp) or direct from SEAI.

Subsets of data extracted from the definitive database will be published in two forms; one for Registered Assessors as a computer-readable file, and the second as publicly available product information – all on an Internet web site (www.seai.ie/harp).  The published data will be updated at monthly intervals.

Manufacturers may submit further data on new products at any time. These applications will be dealt with within an agreed time target.

When Twin Burner Cookers boilers published on the database go out of production, SEAI (or their contractor) should be notified so that the entry can be updated.  The data will still be held so that Registered Assessors can make reference to it as required.

You should be aware that once data relating to a particular boiler has been published, any modifications to that product which may affect its seasonal efficiency rating must be submitted in the form of a clearly identifiable “new” entry complete with a modified model identity.  Product names in the database must be unique, and it is not possible to have two entries with the same conjunction of brand name, model name and qualifier and fuel type.  This is to enable a Registered Assessor to differentiate between the modified and un-modified products in the marketplace.

1.2	EFFICIENCY DATA

The purpose of this database is to hold energy efficiency performance calculations for domestic heating appliances.  These notes are concerned with efficiency data for domestic Twin Burner Cooker boilers fuelled by natural gas, LPG or oil.  Although the database will contain other descriptive and technical details as well, all entries must include a DEAP seasonal efficiency value.  Each entry for a DEAP seasonal efficiency value has an efficiency category defined as follows: -

- Efficiency category 1: Seasonal Efficiency based on certified data

Seasonal efficiency has been calculated by the method from the results of standard efficiency tests required to demonstrate compliance with the Boiler Efficiency Directive, together with other information supplied.  The results of the standard tests have been certified by a suitably qualified Notified Body (i.e. an independent test house deemed competent under European rules for boiler testing) as required for DEAP and have been submitted to SEAI with other supporting details. SEAI will have checked published entries with efficiency category 2 in accordance with their requirements.

- Efficiency category 2: Estimated

Efficiency has been taken from DEAP, based on boiler type. Entries with efficiency category 2 are permitted for obsolete boilers only, which may not comply with the provisions of the Boiler Efficiency Directive.

Note:	Information relating to this category can only be supplied by SEAI

Validity and accuracy of the data within the database are paramount.  Careful scrutiny of the data and the certification submitted by manufacturers, and calculation of Seasonal Efficiency values from it, are essential.  To avoid any doubt or misunderstanding as to the accuracy or validity of any of your supporting efficiency data, we have devised a declaration form [Appendix 4] which should be completed and signed by an authorised signatory from whichever Notified Body carried out the Efficiency Testing required to satisfy the Boiler Efficiency Directive.

It should be noted that in certain cases we are required to seek additional clarification of submitted results (e.g. where very high boiler efficiency results have been reported by the Notified Body).  We would be required to seek further explanation of the methods used to produce this data.  In such circumstances we would expect to see confirmation that the test laboratory has carried out sufficient checking of measurements and calculations to ensure consistency of results.

For Twin Burner Cooker boilers with efficiency category 1 only, the database will indicate an energy efficiency band.  For Twin Burner Cooker boilers with other efficiency categories, the field for the efficiency band will be left blank.

The database also provides a field to hold the energy efficiency class, expected to be defined later in a European Council directive for energy labelling.  This field is to be left blank until the European labelling scheme has been defined.

1.3	PRODUCT IDENTIFICATION

It is essential that descriptions obtained from the database allow a Registered Assessor to identify an installed Twin Burner Cooker boiler reliably. Assessors are not heating experts, and will examine only the information on boilers that is readily visible to the householder.  The route to Twin Burner Cooker boiler identification should be viewed as follows: -

- The product must have a unique description (i.e. distinct from any other product entered, or about to be entered, in the database).  The description is made up of Brand Name, Model Name and Qualifier and Fuel type.

- It must be possible for the Registered Assessor to identify the specific product from readily visible information.

- Readily visible information is considered to be markings/labels on the outer case that can be seen.  In addition markings/labels that can be read by means of a user moveable panel.  A user moveable panel is considered to be one that may be hinged (e.g. flap or door) or a panel that can be removed without the use of tools and is intended to be used by the householder.

- In order to demonstrate that product information is readily visible photographs will need to be supplied clearly demonstrating how the unique product description can be derived as described in 3 above.  No submissions will be accepted where this evidence cannot be supplied.

- In the case of a gas Twin Burner Cooker boiler that may be converted from one gas type to another in situ (e.g. NG to LPG) it is not necessary for the fuel type to be clearly visible.  It is considered possible for the Registered Assessor to determine the fuel type by other means.

The process by which a product description is verified is given in Appendix 3.

It should be noted that where a unique product description cannot be demonstrated (normally by means of photographs) an entry to the database will be denied.

2	Help and Advice on Supplying Twin Burner Cooker Boiler Efficiency Data

2.1	How do I make a submission to the Database?

A submission is made using the data entry forms provided at the back of this guidance booklet.  Detailed advice on completing the main data entry form (Appendix 1) is given in section 2.2.

As well as the basic Twin Burner Cooker boiler data you will need to provide there are a number of accompanying forms and pieces of evidence you will also need to supply.  To help clarify what this is a table is presented below listing the forms you will need in various submission scenarios.  Although this cannot be guaranteed to be exhaustive in all cases it should cover most.

Twin Burner Cooker Boiler Submission Scenarios and Forms/Evidence required

| Forms/Evidence required | Boiler submission scenario |  |  |
| --- | --- | --- | --- |
|  | Boiler tested on fuel it burns | Badged Boiler | LPG Boiler supported by NG efficiency data |
| Manual Data Entry Form (1) |  |  |  |
| Badged Boiler Form (2) | N.A. |  | N.A. |
| Product Identification Photographs (3) |  |  |  |
| Dataplate |  |  |  |
| Boiler Efficiency Directive compliant results declaration (4) |  |  |  |
| LPG Boiler Declaration Form (6) | N.A. | N.A. |  |

Note: Numbers in brackets indicate the Appendix number where the appropriate form or further information can be found.

For each Twin Burner Cooker boiler submitted there must be the accompanying paperwork as indicated in the above matrix.  This applies equally whether or not you make the data submission electronically.  As a further aid a submission checklist is provided in Appendix 8.

It is important that all forms requiring signature (apart from the Notified Body Declarations) be signed by the Technical Director of the submitting company.

2.1	Manual Entry

A set of manual data entry forms is included in Appendix 1 – please photocopy as many as you need for all of your product data.  One complete set of forms should be completed for each Twin Burner Cooker boiler.

Please take great care when writing in each of the boxes.  Special care is needed when recording results from any testing body.  Please note that the accreditation information must be substantiated with appropriate copies of accreditation certificates and test reports (alternatively, your Notified Body may confirm results in a formal signed letter or Declaration as detailed in Appendix 4).  Failure to provide this evidence will prevent your product from receiving its full listing in the database.  Each form contains a signature box for the Technical Director or the equivalent person in your organisation to affirm the quality of the information supplied.  Please note that you are also required to send an actual dataplate for each Twin Burner Cooker boiler submitted.

The data entry form has been designed with subsequent data input in mind.  Overleaf are some explanatory notes to help you fulfil the Government’s requirements.

NB	MANDATORY ENTRIES ARE PRINTED IN BOLD

There is a requirement for consistency in naming (a) your Company (b) the brand and (c) the actual models submitted.  We will be making amendments as and when required to both categories and you should pay particular attention to that when checking your confirmation reports.

Entry 1	Manufacturer Name [up to 50 characters]

This is the name of the Twin Burner Cooker boiler manufacturer or company responsible for the Twin Burner Cooker boiler in the Ireland at the time the Twin Burner Cooker boiler was manufactured – as it appears on the product casing and/or the owners’ instruction leaflets.  Please omit punctuation marks and spaces between initials.  Once we have confirmed a manufacturer name this format will be used for all future entries appearing under that name.

Entry 2	Current Name [up to 50 characters]

This is the current name of the Manufacturer or Company responsible for this Twin Burner Cooker boiler in the Ireland.  This may be different to the original name – if not mark “as above”.

NB	If the same Twin Burner Cooker boiler model is sold under more than one Manufacturer’s name, then you should complete the Twin Burner Cooker Boiler Identity Form in Appendix 3 giving the other identities so that separate entries can be included on the database.

Entry 3	Address [up to 365 characters in total]

This format is as recommended in BS7666: Part 3 Section 2 Table 1 – hence the terminology.  If your company does not have an Irish or UK address, then please try to match the format as closely as possible.

- Secondary addressable object name [e.g. Design Division] - up to 60 characters

- Primary addressable object name [e.g. Big House] - up to 60 characters

- Designated Street name - up to 100 characters

- Locality name [if appropriate] - up to 35 characters

- Town/city name - up to 30 characters

- Administrative area name [e.g. County] - up to 30 characters

- Postcode - up to 20 characters

- Country – if not Ireland or UK - up to 30 characters

Entry 4	Telephone number 	[up to 25 characters]

Entry 5		Website address		[up to 75 characters]

This is the actual home website address for the manufacturer [in the usual www.seai.ie/harp or .com configuration].  It will be used to provide a hotlink from each Twin Burner Cooker boiler record to the specific manufacturer’s website.

Entry 6	Brand Name [up to 50 characters]

This is the name of the product brand.  It is anticipated that this name will reflect the manufacturer name.  It is intended that this field be used for the brand instead of including it in the Model Name (e.g. model name: ACME 123 would be Brand Name: ACME; Model Name 123).

Entry 7	Model Name [up to 50 characters]

This should be the name as it appears on the Twin Burner Cooker boiler casing or leaflet of owners’ instructions.

NB	As highlighted in Entry 2’s notes, separate entries are required for each model if the same Twin Burner Cooker boiler is sold under more than one model or brand name.

Entry 8		Model qualifier [up to 30 characters]:-

This is for recording any special qualifier to the model name, which may have been used to discriminate between different versions of the same model.

Entry 9		Twin Burner Cooker Boiler ID [up to 40 characters]

This is the Twin Burner Cooker boiler identifier which, when used in conjunction with the manufacturer’s name, is unique for the model and all other characteristics affecting efficiency.  Where known, this provides an effective short cut for identification.  It could be the GC (former UK Gas Council) number for gas boilers or OFTEC Registration Number for an oil boiler.  Alternatively, it could be any other unique identifier chosen by the manufacturer and clearly marked on the boiler.  If not known, please leave blank.

Entry 10		First year of manufacture if known [up to 4 characters]

If you do not know, give your best estimate of the year or just leave blank.

Entry 11	Final year of manufacture [up to 8 characters]

Enter “current” if the model is still in production.  If the model is no longer produced, but you do not know the final year of manufacture, then either enter your best estimate of the year or simply enter “obsolete”.

Entry 12	Fuel [1 digit]

| Fuel | Code | Notes |
| --- | --- | --- |
| Gas | 1 | “Gas” means natural gas (mains gas) only |
| LPG | 2 | “LPG” means butane or propane |
| Oil | 4 | “Oil” means kerosene, or gas oil only |

NB	If the same boiler may be used for more than one type of fuel, then a separate entry is required for each fuel type.

Entry 13	Main Type [1 digit]

| Type | Code | Notes |
| --- | --- | --- |
| Regular | 1 | As defined in DEAP (Version 1) (see notes in Appendix 5) – a Regular boiler is a boiler which does not have the capability to provide DHW directly, it may never the less provide DHW indirectly via a separate hot water storage cylinder located outside the boiler. |

Entry 14	Condensing [1 digit]

| Definition | Entry code | Notes |
| --- | --- | --- |
| Non-condensing | 1 | As defined in DEAP (Version 1) (see notes in Appendix 5) - Non-condensing means condensation is not expected [by design] within the boiler. |
| Condensing | 2 | As defined in DEAP (Version 1) (see notes in Appendix 5) - Condensing means a boiler designed to make use of the latent heat in the combustion products by condensing water vapour within the appliance. The boiler must allow the condensate to leave the heat exchanger in liquid form by way of a condensate drain. |

Entry 15	Flue Type [1 digit]

| Definition | Entry code | Notes |
| --- | --- | --- |
| Open | 1 | Open flued: The boiler will take its combustion air from the room, and discharge outside of the room |
| Room-Sealed | 2 | Room sealed: The boiler air supply and point of discharge of the flue system are outside of the room in which the boiler is installed. |
| Either | 3 | Where a boiler can operate with both an open or room-sealed flue and the dataplate makes no distinction. |

Entry 16	Fan Assistance [1 digit]

| Definition | Entry code | Notes |
| --- | --- | --- |
| No-fan | 1 |  |
| Fan | 2 | A fan assisted boiler is a boiler with a fan designed to supply air or remove products of combustion. |

Entry 17	Boiler Power (bottom of range)

[number of up to 7 characters - e.g. nnn.nnn]

For a boiler with a single rated output, this figure should be the nominal output power (to water) of the boiler in kW.  (Note: If the boiler is modulating then this power MUST be the same as the Boiler Power (top of range) as recorded in Entry 21)

For range rated boiler this should be the minimum output power of the range declared by the manufacturer.

Entry 18	Boiler Power (top of range)

[number of up to 7 characters - e.g. nnn.nnn]

For a single output boiler this figure should be the nominal output power (to water) of the boiler in kW i.e. the same as Entry 20.

For range rated boiler this should be the maximum output power of the range declared by the manufacturer.

Boilers with heat outputs greater than 70kW are not permitted on the database.

(Note: If the power is only available in BTU/hr then it should be converted using the factor 1BTU/hr = 0.000293kW.)

Entry 19	Case Loss at Full Output

[number of up to 7 characters - e.g. nnn.nnn]

The case loss from the product, measured in kW, when the boiler part only is operating at full output power.  This must not include contribution from the cooker part.

Entry 20	Heat to Water at Full Load

[number of up to 7 characters - e.g. nnn.nnn]

This is defined as the heat to water power of the boiler alone, measure in kW, at full load (at which the case loss has been measured).  This is ɸ water as defined in Section D5 of DEAP manual.

Entry 21	DEAP Equation Used to Calculate the Seasonal Efficiency

[up to 3 digits]

The number of the equation used to calculate the seasonal efficiency.  There are very clearly defined rules [DEAP (Version 1)] regarding these calculations.  Full details of the equations, procedures and rules are given in Appendix 5.

## Entry 22	DEAP seasonal efficiency [number up to 4 characters]

Note:	SEAI (or their delegate) will calculate this figure and notify manufacturers of their results during a 7-day checking period.

This may be entered by the manufacturer or left blank.  If entered, it must be obtained using the methods indicated in entry 21 (rounded to the nearest 0.1%).

Entry 23	Efficiency Category [1 digit]

| Definition | Entry code | Notes |
| --- | --- | --- |
| HARP | 1 | Not currently used. |
| HARP | 2 | Calculated from certified data. |

Entry 24	Test gas for LPG

It is intended to identify those LPG boilers for which efficiency test results from a NG derivative have been supplied by means of this field.

| Definition | Entry code | Notes |
| --- | --- | --- |
| Not applicable | Blank | If this category does not apply to boiler in question. |
| Test gas is LPG | 0 | If the efficiency tests from which seasonal efficiency was calculated were carried out using LPG test gas. |
| Test gas is NG | 1 | If the efficiency tests from which seasonal efficiency was calculated were carried out using NG test gas and the modified calculation procedures (see DEAP (Version 1)). |

Entry 25	Full load efficiency [number up to 5 characters to one decimal place e.g. nnn.n]

This is the certified net efficiency at full load (as defined in Schedule 2 of the Boiler Efficiency Directive).  Supporting evidence may be:-

- A copy of the BED or CE certificate (or original signed declaration) as issued by an EU Notified Body clearing showing the test results, or

- A declaration issued and authorised by an appropriate EU Notified Body showing the boiler efficiency results for the model submitted.  A declaration form is provided for this purpose (see Appendix 4)

The certificate or declaration shall clearly indicate the model to which it applies.  If this model differs in any way (either physically or by model name or other identifier) from that shown on the certificate, the attached Boiler Identity Form (Appendix 2) shall be used to clearly identify all of these differences.  This form shall be completed and signed as indicated.

Entry 26	Part Load efficiency

[number up to 5 characters to one decimal place e.g. nnn.n]

This is the certified net efficiency at part load (as defined in schedule 2 of the Boiler Efficiency Directive).  Supporting evidence may be:-

- A copy of the BED or CE certificate (or original signed declaration) as issued by an EU Notified Body clearing showing the test results, or

- A declaration issued and authorised by an appropriate EU Notified Body showing the boiler efficiency results for the model submitted.  A declaration form is provided for this purpose (see Appendix 4)

The certificate shall clearly indicate the model to which it applies.  If this model differs in any way (either physically or by model name or other identifier) from that shown on the certificate, the Boiler Identity Form (Appendix 2) shall be used to clearly identify all of these differences.  This form shall be completed and signed as indicated.

Entry 27	Boiler type for ple test [1 digit]

As defined in Schedule 2 of Statutory Instrument 1993 No 3083 (Energy Conservation) The Boiler (Efficiency) Regulations and Council Directive 92/42/EEC.

| Definition | Entry code | Notes |
| --- | --- | --- |
| ST = Standard | 1 |  |
| LT = Low-temp | 2 | Includes condensing boilers using liquid fuel |
| GC = Gas condensing | 3 |  |

Entry 28	Ignition [1 digit]

Whether or not the boiler has a permanent pilot light

| Definition | Entry code | Notes |
| --- | --- | --- |
| No | 1 | Boiler does not have a permanent pilot light |
| Yes | 2 | Boiler has a permanent pilot light |

Entry 29	Burner Control [1 digit]

| Definition | Entry code | Notes |
| --- | --- | --- |
| On-Off | 1 | This excludes a boiler with the capability to vary the fuel burning rate while maintaining continuous firing |
| Variable | 2 | This includes a boiler with the capability to vary the fuel burning rate while maintaining continuous firing |

Entry 30	Electrical Power [up to 4 digits]

| Definition | Entry code | Notes |
| --- | --- | --- |
| Boiler on | Input actual value (W) | This is the average electrical power consumed while the boiler is firing at its highest rating, in Watts. This includes fans, motors, heaters and other electrical equipment but should exclude any pump used to circulate water outside the boiler. |

Entry 31	Electrical Power [up to 4 digits]

| Definition | Entry code | Notes |
| --- | --- | --- |
| Boiler off | Input actual value (W) | This is the average electrical power consumed while the boiler is adjusted to fire at its highest rating (but is not firing), in Watts. This includes fans, motors, heaters and other electrical equipment but should exclude any pump used to circulate water outside the boiler |

Entry 32	Trade Association [up to 50 characters]

The name of the Trade Association representing the appliance type submitted.

Entry 33	Run Time Indicator

| Definition | Entry code | Notes |
| --- | --- | --- |
| Unknown/Not Applicable | Leave blank |  |
| No Run Time Indicator | 0 |  |
| Run Time Indicator Present | 1 |  |

Entry 34	Date

Date that form is submitted.

Entry 35-38	Name, Position, E-mail address & Signature of Person completing form

Is should be noted that this form must be signed by the Technical Director or equivalent of the company making the submission.  If someone other then the Technical Director signs the forms it is a requirement that suitable documentary evidence of the authority of the signatory is provided.

## Appendix 1

## Manual Data Entry

## Form

[one to be completed for each Twin Burner Cooker boiler model submitted]

# HOME-HEATING APPLIANCES REGISTER OF PERFORMANCE (HARP) DATABASE

Data Entry and Declaration Form

### DOMESTIC TWIN BURNER COOKER BOILERS

One to be completed for each Solid Fuel boiler type you wish to appear on the HARP Database – please photocopy as many forms as you require).

NB	MANDATORY ENTRIES ARE PRINTED IN BOLD

| Entry No | Entry Title |  |  | Entry Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Manufacturer Name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Current Name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Address |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## Second addressable object name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## Primary addressable object name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Designated Street name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## Locality name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Town/City name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## Administrative area name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Postcode |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Country (if not UK) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Telephone No |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Manufacturer’s Website Address |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Brand Name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Model Name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Model Qualifier |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Product ID |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## First Year of Manufacture |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Final Year of Manufacture |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Fuel |  |  | 1 |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 4 |  |  |  |  |
|  | Main Type |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Condensing |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |
|  | Flue Type |  |  | 1 |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 3 |  |  |  |  |
|  | Fan assistance |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |
|  | Boiler Power (Bottom-of-range) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | kW |  |  |  |  |  |
|  | Boiler Power (Top-of-range) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | kW |  |  |  |  |  |
|  | Case Loss at Full Output |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | kW |  |  |  |  |  |
|  | Heat to Water at Full Output |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | kW |  |  |  |  |  |
|  | DEAP Equation appropriate |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## DEAP Seasonal Efficiency |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ## % |  |  |  |  |  |
|  | ## Efficiency Category |  |  |  | ## 1 |  |  |  |  |  |  | ## 2 |  |  |  |  | ## 3 |  |  |  |  |  | ## 4 |  |
|  | ## Test gas for LPG |  |  |  | ## 0 |  |  |  |  |  |  |  |  |  |  |  | ## 1 |  |  |  |  |  |  |  |
|  | ## Full Load Efficiency |  |  |  | ## (net) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Part Load Efficiency |  |  |  | ## (net) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Boiler type for ple test |  |  |  | ## 1 |  |  |  |  |  |  |  |  | ## 2 |  |  |  |  |  |  | ## 3 |  |  |  |
|  | ## Ignition |  |  |  | ## 1 |  |  |  |  |  |  |  |  |  |  |  | ## 2 |  |  |  |  |  |  |  |
|  | ## Burner Control |  |  |  | ## 1 |  |  |  |  |  |  |  |  |  |  |  | ## 2 |  |  |  |  |  |  |  |
|  | ## Electrical Power* (Firing) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ## Watts |  |  |  |  |  |  |  |
|  | ## Electrical Power* (Not-Firing) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ## Watts |  |  |  |  |  |  |  |
|  | ## Trade Association |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Run Time Indicator |  |  |  | ## 0 |  |  |  |  |  |  |  |  | ## 1 |  |  |  |  |  |  | ## 2 |  |  |  |
| ## THIS SHADED SECTION MUST BE COMPLETED FOR ALL SUBMISSIONS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## Cooker Boiler Type (circle appropriate category) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## ST |  |  | ## LT |  |  |  |  |  |  |  |  |  | ## GC |  |  |  |  |  |  |  |  |  |  |  |
| ## Note = Standard Boiler |  |  | ## Note = Low Temperature or Liquid Fuel Condensing Boiler |  |  |  |  |  |  |  |  |  | ## Note = Gas Condensing |  |  |  |  |  |  |  |  |  |  |  |
| ## Product Identification (please circle)* |  |  |  |  |  | ## 1a |  |  |  | ## 1b |  |  |  |  | ## 1c |  |  | ## 2d |  |  |  | ## 2e |  | ## 2f |
|  | ## Date of Submission |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Name of Submitter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Submitter E-mail Address |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Position of Submitter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Signature of Submitter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## Notes | * | ## Please identify how product is identified (refer to Appendix 3 for criteria) and circle those combinations that apply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

By signing this form I also declare that all the other information included in my returns are correct and that I am the Technical Director (or equivalent).

### Appendix 2

Badged Twin Burner Cooker Boiler Form

[one to be completed for each badged boiler submitted & signed by Technical Director or equivalent]

[Please note that an actual dataplate for each model submitted is required]

### HOME-HEATING APPLIANCES REGISTER OF PERFORMANCE (HARP) DATABASE

### “Badged” Twin Burner Cooker Boiler Form

(Please photocopy as many as you require)

| Declaration of Similarity for “Badged” Products |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| This form confirms that the boiler (termed the “Badged model”) is the same in all material respects (excluding cover) including thermal performance as a boiler (termed the “Master model”) for which a BED Certificate is available from a Notified Body |  |  |  |  |  |  |  |
| Name of “Master Brand” | Name of “Master Model” |  |  |  |  | “Master Model” Qualifier. |  |
| Name of “Badged Brand” | Name of “Badged Model” |  |  |  |  | “Badged Model” Qualifier. |  |
| Bagded Model Boiler Power |  | Lowest rating (kW) |  |  | Highest rating (kW) |  |  |
| Are the two boilers currently made in the same factory? |  |  |  |  |  |  | #### YES |
|  |  |  |  |  |  |  | NO |
| If NO, or if the “Master Model” is out of production please enclose details of any QA system that is in place to ensure product quality and similarity. |  |  |  |  |  |  |  |
| I hereby confirm that the “Badged Model” listed above has the same thermal performance as the “Master Model”. |  |  |  |  |  |  |  |
| Signature |  |  | Date |  |  |  |  |
| Name (Please print) |  |  | Position |  |  |  |  |

### Appendix 3

Product Identification Route

[Please note that an actual dataplate for each model submitted is required]

Route to Product Identification

As described in section 1.2 it is essential that Registered Assessors can readily identify boilers.  To this end a mechanism has been devised to assist in the confirmation that a boiler can be easily identified.

Firstly the means of identifying the boiler needs to be established.  It is anticipated that the following sets of circumstances may apply to most boiler products:-

- What product information is shown on the boiler case?  Is it:

- Full brand and model name and qualifier, giving unique description of this product

- Partial brand and name information

- No brand and name information

- What product information is visible (by means of a moveable or removable panel) and accessible (without the use of tools) to the householder? Is it:

- Full brand and model name and qualifier, giving unique description of this product

- Partial brand and name information which together with 1b gives unique description of this product

- No brand and name information, or insufficient to provide a unique description

“Unique” means distinct from any other product entered, or about to be entered, in the database.

In order to meet unique description requirements applications can only be accepted in the following circumstances:

1a OR 1b + 2d or 1b + 2e OR 1c + 2d

In any of the above cases photograph(s) should be provided to demonstrate that the product description can be verified by these routes.

In all other circumstances (i.e., 1b + 2f, or 1c + 2f) applications will be refused, as it will considered that in such cases the Registered Assessor will not be able to readily identify the product.

### Appendix 4

Notified Body Efficiency Declaration Form

[to be completed as an alternative to

copies of actual

technical report sheets]

DECLARATION MADE BY

[Insert Name of Notified Body]

ON BEHALF OF

[Insert Name of Manufacturer]

| Tests performed on LPG/NG see note below | Original Twin Burner Cooker Boiler Name | Ireland Market Name | Full Load Efficiency (%, net) | Part Load Efficiency (%, net) |
| --- | --- | --- | --- | --- |

Boilers marked with an asterisk[*] are LPG models where the tests were carried out using Natural Gas [G20].

We declare that the full and part load efficiency test results detailed above have been obtained by means deemed to satisfy the Boiler Efficiency Directive (92/42/EEC).  The water temperature criteria defined in the Boiler Efficiency Directive [see below] have been satisfied in obtaining these results.

| Type of Boiler | Range of Power | Efficiency at rated output | Efficiency at part load |
| --- | --- | --- | --- |
|  | kW | Average boiler-water temperature | Average boiler-water temperature |
| Standard boilers | 4 to 400 | 70C | ≥ 50C |
| Low temperature boilers1 | 4 to 400 | 70C | 40C |
| Gas condensing boilers | 4 to 400 | 70C | 30C 2 |

1 Including condensing boilers using liquid fuels.

2 Temperature of boiler water supply.

Signed on behalf of [Insert name of Notified Body]:	_______________________________

Date:							_______________________________

Print Name:						_______________________________

Position:						_______________________________

Insert Notified Body Official Stamp if available and/or use official headed paper

### Appendix 5

DEAP Calculations

[the seasonal efficiency procedure explained]

# Extracted from “Dwelling Energy Assessment Procedure (DEAP) (Version 1)”

# Appendix D: Method of determining seasonal efficiency values for gas and oil boilers

Note: The data and equations in this appendix are not to be used by Registered Assessors.

This appendix sets out, in D2 and D4, the method to be used by manufacturers to determine the Home-Heating Appliance Register of Performance (HARP) for particular gas and oil boilers when test data have been obtained to establish conformity with Council Directive 92/42/EEC*.

Manufacturers’ declarations of HARP values so calculated should be accompanied by the form of words in D3, and Registered Assessors should look for the same form of words in order to ascertain that the efficiency value referred to is appropriate for DEAP calculations. The SEDBUK efficiency for SAP calculations in the UK is equally acceptable.

Range cooker boilers with twin burners are covered by D5 and D6.

D1	Definitions

D1.1	Boiler

A gas or liquid fuelled appliance designed to provide hot water for space heating. It may (but need not) be designed to provide domestic hot water as well.

D1.2	Condensing boiler

A boiler designed to make use of the latent heat released by the condensation of water vapour in the combustion flue products. The boiler must allow the condensate to leave the heat exchanger in liquid form by way of a condensate drain. ‘Condensing’ may only be applied to the definitions D1.3 to D1.14 inclusive. Boilers not so designed, or without the means to remove the condensate in liquid form, are called ‘non-condensing’.

D1.3	Regular boiler

A boiler which does not have the capability to provide domestic hot water directly (i.e. not a combination boiler). It may nevertheless provide domestic hot water indirectly via a separate hot water storage cylinder.

D1.4	On/off regular boiler

A regular boiler without the capability to vary the fuel burning rate whilst maintaining continuous burner firing. This includes those with alternative burning rates set once only at time of installation, referred to as range rating.

D1.5	Modulating regular boiler

A regular boiler with the capability to vary the fuel burning rate whilst maintaining continuous burner firing.

D1.6	Combination boiler

A boiler with the capability to provide domestic hot water directly, in some cases containing an internal hot water store.

D1.7	Instantaneous combination boiler

A combination boiler without an internal hot water store, or with an internal hot water store of capacity less than 15 litres.

D1.8	 On/off instantaneous combination boiler

An instantaneous combination boiler that only has a single fuel burning rate for space heating. This includes appliances with alternative burning rates set once only at time of installation, referred to as range rating.

D1.9	Modulating instantaneous combination boiler

An instantaneous combination boiler with the capability to vary the fuel burning rate whilst maintaining continuous burner firing.

D1.10	Storage combination boiler

A combination boiler with an internal hot water store of capacity at least 15 litres but less than 70 litres,

OR

a combination boiler with an internal hot water store of capacity at least 70 litres, in which the feed to the space heating circuit is not taken directly from the store. If the store is at least 70 litres and the feed to the space heating circuit is taken directly from the store, treat as a CPSU (D1.13 or D1.14).

D1.11	On/off storage combination boiler

A storage combination boiler that only has a single fuel burning rate for space heating. This includes appliances with alternative burning rates set once only at time of installation, referred to as range rating.

D1.12	Modulating storage combination boiler

A storage combination boiler with the capability to vary the fuel burning rate whilst maintaining continuous burner firing.

D1.13	On/off combined primary storage unit (CPSU)

A single appliance designed to provide both space heating and the production of domestic hot water, in which there is a burner that heats a thermal store which contains mainly primary water which is in common with the space heating circuit. The store must have a capacity of at least 70 litres and the feed to the space heating circuit must be taken directly from the store. The appliance does not have the capability to vary the fuel burning rate whilst maintaining continuous burner firing. This includes those with alternative burning rates set once only at time of installation, referred to as range rating.

D1.14	Modulating combined primary storage unit (CPSU)

A single appliance designed to provide both space heating and the production of domestic hot water, in which there is a burner that heats a thermal store which contains mainly primary water which is in common with the space heating circuit. The store must have a capacity of at least 70 litres and the feed to the space heating circuit must be taken directly from the store. The appliance has the capability to vary the fuel burning rate whilst maintaining continuous burner firing.

D1.15	Low temperature boiler

A non-condensing boiler designed as a low temperature boiler and tested as a low temperature boiler as prescribed by the Boiler Efficiency Directive (i.e.; the part load test was carried out at average boiler temperature of 40°C).

D1.16	Keep-hot facility

A facility within an instantaneous combination boiler whereby water within the boiler may be kept hot while there is no demand. The water is kept hot either (i) solely by burning fuel, or (ii) by electricity, or (iii) both by burning fuel and by electricity, though not necessarily simultaneously.

D2	Method for calculating the Home-Heating Appliance Register of Performance (HARP)

The method of calculation is applicable only to boilers for which the full load and the 30% part load efficiency values, obtained by the methods deemed to satisfy Council Directive 92/42/EEC, are available. These are net efficiency values. It is essential that both test results are available and that the tests are appropriate to the type of boiler as defined in Council Directive, otherwise the calculation cannot proceed.

In the calculation method the data are first converted to gross efficiency under test conditions, and then converted to a seasonal efficiency value that applies under typical conditions of use in a dwelling, allowing for standing losses.

In this Appendix, efficiencies are expressed in percent. Intermediate calculations should be done to at least four places of decimals of a percentage, and the final result rounded to one decimal place.

The procedure to be adopted by manufacturers is as follows:

1. Determine fuel for boiler type.

The fuel for boiler type must be one of natural gas, LPG (butane or propane), or oil (kerosene or gas oil). HARP cannot be calculated for other fuels.

2. Obtain test data.

Retrieve the full-load net efficiency and 30% part-load net efficiency test results. Tests must have been carried out using the same fuel as the fuel for boiler type, except as provided in D4.

3. Reduce to maximum net efficiency values.

Table D2.1 gives the maximum values of net efficiency for each fuel that may be used for the purposes of the DEAP. Reduce any greater test value to the appropriate value given in Table D2.1.

- Table D2.1: Maximum net efficiency values (in %)

| Condensing boilers |  | Non-condensing boilers |  |
| --- | --- | --- | --- |
| Full load | 30% part load | Full load | 30% part load |
| 101.0 | 107.0 | 92.0 | 91.0 |

4. Convert the full and 30% part load efficiencies from net values to gross.

Use the following equation with the appropriate factor from Table D2.2.

Egross =  f × Enet

- Table D2.2 : Efficiency conversion factors

| Fuel | Net-to-gross conversion factor, f |
| --- | --- |
| Natural gas | 0.901 |
| LPG (propane or butane) | 0.921 |
| Oil (kerosene or gas oil) | 0.937 |

5. Categorise the boiler.

- Select the appropriate category for the boiler according to the definitions given in D1.

- If a gas or LPG boiler, determine whether it has a permanent pilot light:

if it has a permanent pilot light, set p = 1

if not, set p = 0.

- In the case of a storage combination boiler (either on/off or modulating) determine from the test report whether the losses from the store were included in the values reported (this depends on whether the store was connected to the boiler during the tests):

if the store loss is included, set b = 1

if not, set b = 0.

- In the case of a storage combination boiler or a CPSU, obtain the store volume, Vcs, in litres from the specification of the device and the standby loss factor, L, using the following equation:

if t < 10 mm: L = 0.0945 – 0.0055t

if t  10 mm: L = 0.394/t

where t is the thickness of the insulation of the store in mm.

6. Calculate seasonal efficiency

a)	Use the boiler category and other characteristics as defined in D1 (non-condensing or condensing; gas or LPG or oil; on/off or modulating) to look up the appropriate HARP equation number in Table D2.3. If no equation number is given the calculation cannot proceed. Otherwise, select the appropriate equation from Table D2.4 or Table D2.5.

b)	Substitute the gross full and part load efficiencies (found in step 4) and p, b, V and L (found in step 5). Round the result to one decimal place; i.e., to nearest 0.1%. Note the result as [x] for the purpose of the declaration in D3.

Table D2.3: Boiler category table

| HARP Equation numbers for different boiler types | non-condensing (see D1.2) |  |  |  | low-temperature (seeD1.15) | condensing (see D1.2) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Gas or LPG |  | Oil |  |  | Gas or LPG |  | Oil |  |
|  | on/off (see D1.4, D1.8, D1.11, D1.13) | modulating (see D1.5, D1.9, D1.12, D1.14) | on/off (see D1.4, D1.8, D1.11) | modulating (see D1.5, D1.9, D1.12) |  | on/off (see D1.4, D1.8, D1.11, D1.13) | modulating (see D1.5, D1.9, D1.12, D1.14) | on/off (see D1.4, D1.8, D1.11) | modulating (see D1.5, D1.9, D1.12) |
| regular boiler (see D1.4, D1.5) | 101 | 102 | 201 | X | X | 101 | 102 | 201 | X |
| instantaneous combi boiler (see D1.7, D1.8, D1.9) | 103 | 104 | 202 | X | X | 103 | 104 | 202 | X |
| storage combi boiler (see D1.10, D1.11, D1.12) | 105 | 106 | 203 | X | X | 105 | 106 | 203 | X |
| combined primary storage unit (see D1.13, D1.14) | 107 | 107 | X | X | X | 107 | 107 | X | X |

- Table D2.4: Seasonal efficiency, E, for natural gas and LPG boilers

| Gas or LPG boiler type | Eq. no. | Equation |
| --- | --- | --- |
| D1.4 : On/off regular | 101 | E = 0.5(Efull + Epart) – 2.5 – 4p |
| D1.5 : Modulating regular | 102 | E = 0.5(Efull + Epart) – 2.0 – 4p |
| D1.8 : On/off instantaneous combination | 103 | E = 0.5(Efull + Epart) – 2.8 – 4p |
| D1.9 : Modulating instantaneous combination | 104 | E = 0.5(Efull + Epart) – 2.1 – 4p |
| D1.11 : On/off storage combination | 105 | E = 0.5(Efull + Epart ) – 2.8 + (0.209 × b × L × Vcs) – 4p |
| D1.12 : Modulating storage combination | 106 | E = 0.5(Efull + Epart ) – 1.7 + (0.209 × b × L × Vcs) – 4p |
| D1.13 : On/ off combined primary storage unit (condensing and non-condensing) D1.14 : Modulating combined primary storage unit (condensing and non-condensing) | 107 | E = 0.5(Efull + Epart ) – (0.539 × L × Vcs) – 4p |

- Table D2.5: Seasonal efficiency, E, for oil boilers

| Oil boiler type | Eq. No. | Equation |
| --- | --- | --- |
| D1.3 : Regular | 201 | E = 0.5(Efull + Epart) |
| D1.7 : Instantaneous combination | 202 | E = 0.5(Efull + Epart) – 2.8 |
| D1.10 : Storage combination | 203 | E = 0.5(Efull + Epart ) – 2.8 + (0.209 × b × L × Vcs) |

D3	Declaring values of seasonal efficiency

Manufacturers wishing to declare their products' seasonal efficiencies for the specific purposes of calculating DEAP ratings can do so provided that:

a) They use the HARP calculation procedure given in D2 above; and

b)   the necessary boiler test data and the calculations are certified by a Notified Body accredited for the testing of boilers by an EU national accreditation service. The Notified Body must certify that: ‘the full load and part load efficiency test results detailed in [insert reference to report on the efficiency tests] have been obtained by methods deemed to satisfy the Boiler Efficiency Directive’.

Where a manufacturer declares the HARP, it shall be expressed as:

“Seasonal Efficiency (HARP) = [x]%

The value is used in the Irish Government’s Standard Assessment Procedure (DEAP) for energy rating of dwellings. The test data from which it has been calculated have been certified by  [insert name and/or identification of Notified Body].”

Data for several products may be presented in tabulated form, in which case the second paragraph of the declaration should be incorporated as a note to the table.

D4	Method for calculating the HARP for boilers fuelled by LPG but tested with natural gas

If the fuel for boiler type is LPG but the fuel used to obtain efficiency test results is natural gas then HARP may be calculated subject to certain conditions using the procedure given below. The value of HARP will be lower than if the fuel used to obtain the test results had been LPG.

1. Note the restrictions set out at the start of D2, which still apply.

2. Any differences between the boiler fuelled by natural gas (used to obtain full-load and 30% part-load efficiency test results) and the boiler fuelled by LPG (for which the HARP is required) must be minor. Examples of minor differences are a change of gas injector or adjustment by a single screw on the gas valve.

3. Determine the net heat input on a net calorific value basis for both the natural gas boiler and the LPG boiler. The LPG figure must lie within ± 5% of the natural gas figure.

4. Determine by measurement the percentage dry CO2 by volume at the maximum heat input for both the natural gas boiler and the LPG boiler. From the results calculate the excess air fractions for both boilers. The calculated excess air fraction for the LPG boiler must not exceed that for the natural gas boiler by more than 5% (of the natural gas excess air fraction).

5. Retrieve the full-load net efficiency and 30% part-load net efficiency test results. If the boiler is a condensing boiler then deduct 2.2 percentage points from the 30% part-load net efficiency test result.

6. Follow the calculation procedure in D2 from step 3 onwards, taking the fuel for boiler type as LPG.

D5	Method for calculating Seasonal Efficiency and Case Emission value of a non-condensing twin-burner range cooker boiler

1.	The method of calculation of the Seasonal Efficiency is applicable only to cooker boilers for which the full load and the 30% part load efficiency values for the boiler function, obtained by the methods deemed to satisfy Council Directive 92/42/EEC, are available.

Note: A non-condensing range cooker boiler which does not have the capability to provide domestic hot water directly (i.e. is not a combination boiler), but which may nevertheless provide domestic hot water indirectly via a separate hot water storage cylinder exactly matches the definition D1.3 for a Regular Boiler. Consequently the methods deemed to satisfy 92/42/EEC for a Regular Boiler will equally satisfy this requirement for the equivalent type of range cooker boiler.

These efficiencies are for the heat transferred to water and are carried out with the cooker burner turned off,

When undertaking the efficiency test, record

-	input power (net) at full load conditions, Φinput,net, in kW.

-	heat transfer to the water under full load conditions, Φwater, in kW

-	flue loss (net) under full load conditions, Φflue,net, in kW according to the method given in EN 304:1992 + Amendment 1: 1998 or other method assured by the independent test laboratory as providing comparable results for the product under test.

2. 	Calculate the HARP according to D2 using the appropriate equation for a regular boiler.

3. 	Calculate the case heat emission at full load from: -

Φcase = Φinput,net – Φwater -Φflue,net

where	Φwater is the heat transferred to water under full load conditions;

Φflue,net is the flue gas loss measured according to BS EN 304.

4. 	If Φcase < 0.2 kW and the case temperatures of the range cooker are below 80°C, the case emission may, as an alternative, be derived from measurements of the case temperatures according to Supplement 1 to OFTEC Standard OFS A101, subject to a maximum figure of Φcase = 0.2 kW.
Note: Supplement 1 to OFTEC Standard OFS A101 (applicable for oil and gas) can be obtained from OFTEC (Oil Firing Technical Association), Tel 0845 6585080, Fax 0845 6585181, e-mail enquiries@oftec.org

5. 	If Φcase exceeds either of  0.05 × Φwater or 1 kW, reduce Φcase to 0.05 × Φwater or 1 kW (whichever is the smaller).

6.	Provide the values of Φcase and Φwater in kW as part of the test report.

D6	Declaring values of seasonal efficiency and heat emission from the case for twin-burner range cooker boilers

Manufacturers wishing to declare their products’ seasonal efficiencies and case emission values for the specific purposes of calculating DEAP ratings can do so provided that:

- They use the calculation procedure given in D5 above; and

- The necessary boiler test data and calculations are certified by an independent Test Laboratory notified under the Council Directive 92/42/EEC on efficiency requirements for new hot-water boilers fired with liquid or gaseous fuels (known as a “Notified Body”).

Where a manufacturer declares the seasonal efficiency and the case emission value, it shall be expressed as:-

Seasonal Efficiency (HARP) = [x]%

Case heat emission at full load = [y] kW

Heat transfer to water at full load = [z] kW

The values are used in the Irish Government’s Standard Assessment Procedure (DEAP) for the energy rating of dwellings.   The test data from which they have been calculated has been certified by [insert name and/or identification of Notified Body].

Data for several products may be presented in tabulated form, in which case the last paragraph of the declaration should be incorporated as a note to the table.

### Appendix 6

LPG Declaration Form

### HOME-HEATING APPLIANCES REGISTER OF PERFORMANCE (HARP) DATABASE

## The LPG Twin Burner Cooker Boiler Declaration Form (Page 1 of 2)

(Please photocopy as many as you require)

| ##### Declaration of LPG Boiler information (based on NG test data) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### LPG Model Name | LPG Model Qualifier |  |  |  |  |  |  |  |
| NG Model Name (for which test data used for LPG entry) |  | NG Model Qualifier (for which test data used for LPG entry) |  |  |  |  |  |  |
| The following information is declared in order to satisfy the requirements of paragraph D4 of DEAP (Version 1) and thus allow LPG entry to be made on the basis of NG boiler efficiency test data: |  |  |  |  |  |  |  |  |
| - I confirm that the difference between the NG and LPG boilers described above are minor (e.g. different injector, gas value adjustment.) |  |  |  |  |  | Yes |  | No |
| - The net heat input of the LPG boiler lies within 5% of the NG boiler. |  |  | NG Heat Input (net kW) |  | LPG Heat Input (net kW) |  |  |  |
| - Attached to this form is evidence of the measurements made to determine the percentage dry CO2 by volume at the max. Heat input for both the NG and LPG boilers. This shows the calculation process undertaken to determine the excess air fractions and demonstrate that excess air fraction for the LPG boiler does not exceed that for the natural gas boiler by more than 5%. |  |  |  |  |  | Yes | No |  |
| Signature |  |  |  | #### Date |  |  |  |  |
| Name (Please print) |  |  |  | Position |  |  |  |  |

## HOME-HEATING APPLIANCES REGISTER OF PERFORMANCE (HARP) DATABASE

## The LPG Twin Burner Cooker Boiler Declaration Form (Page 2 of 2)

(Please photocopy as many as you require)

Evidence of CO2 measurements & Excess air calculations to demonstrate comparability between NG & LPG boilers described on Page 1 of this form

### Appendix 7

Submission Check List

| Twin Burner Cooker Boiler Data Submission Check-list |  |  |
| --- | --- | --- |
| For each boiler model you submit, please check that you have included all relevant data and supporting evidence as follows:- |  |  |
| Form or method of data submission | Where you can find it |  |
| Manual Data Entry and Declaration Form | Appendix 1 |  |
| Twin Burner Cooker Boiler Identity Form - your declaration of similarity for “Badged” products | Appendix 2 |  |
| An actual example of the Twin Burner Cooker Boiler dataplate (i.e. the plate or label fixed to the appliance) | In your product’s technical file |  |
| Photographic Evidence of Twin Burner Cooker boiler identification (i.e. photos clearly showing how the product is uniquely identified by the Registered Assessor – making clear whether they are visible [on the case or via accessible control panel]) | See Appendix 3 |  |
| Extract(s) from Technical Report recording efficiency data as measured [Note: this must include independent certified evidence from a Notified Body that the efficiency data presented was measured in accordance with the methods required by the Boiler Efficiency Directive] | In your product’s technical file |  |
| In absence of above, we can accept a signed declaration of results from the Notified Body which carried out the tests | Appendix 4 |  |
| Copy of CE Certificate for the model submitted | In your product’s technical file |  |
| The LPG Boiler Declaration Form (if required) – submission is for a LPG boiler for which NG test results are to be used | Appendix 6 |  |
| Please Note: The working language of the database is English – submissions from International Notified Bodies should include translations into English |  |  |

### Note:  Those items that are mandatory requirements for each boiler application are highlighted in bold print

### Appendix 8

List of Heating Products published on the HARP Database

List of Heating Products published on the HARP Database

- Gas & Oil Boilers

- Cooker Boilers

- Solid Fuel Boilers

- Micro CHP

- Heat Pumps

- Solar Heating Appliances

All of the above listed products are published on the HARP Database.

Separate Submission Guidance Notes are available for each of these product types.  These Guidance Notes may be obtained either from SEAI direct or via the website www.seai.ie/harp.

### Appendix 9

Glossary of Terms

Glossary of Terms

| Term | Definition |
| --- | --- |
| Badged Twin Burner Cooker Boiler | A Twin Burner Cooker Boiler that is sold under a different name but is identical in all technical & performance characteristics to the master model (see below) |
| BED | Boiler Efficiency Directive |
| BER | Building Energy Rating as required to meet Article 7 of the EBPD (this includes a BER Label and BER Advisory Report) |
| DEAP | Dwellings Energy Assessment Procedure |
| EPBD | Energy Performance of Buildings Directive 2002/91/EC |
| HARP Database | The Home-heating Appliance Register of Performance Database |
| Master Twin Burner Cooker Boiler | The original Twin Burner Cooker Boiler from which badged boilers are derived. The badged boiler differs in name only – all performance & technical characteristics are identical to the Master Boiler |
| Registered Assessor | A DEAP software user that is registered with the National EPBD Administration System as an official BER Assessor |
| SEAI | The Sustainable Energy Authority of Ireland |
| User | Any person that uses the HARP Database, including Registered Assessors, public authority personnel, administrators or any other persons |

* Council Directive 92/42/EEC on efficiency requirements for new hot-water boilers fired with liquid or gaseous fuels. Official Journal of the European Communities No L/167/17. 21 May 1992, p. 92