## Cover Sheet
Workbook Information
File Name: | SEAI Flexible electric heating report TES Supporting Data July-2026
Description of file: | Supporting data on Thermal Energy Storage technology cost and performance gathered as part of the 2026 SEAI study on flexibile electric heating technologies
Version | V1.0
Issued: | 2026-07-01

## TES Performance & Costs
Sustainable Energy Authority of Ireland - Flexible Electric Heating Technologies Report 2026
D3.1.1.3: Excel sheet summarising cost and performance parameters of storage technologies
Table below summarises the cost and performance parameters of thermal energy storage technologies collected during the literature review.
Summary of cost and performance data for thermal energy storage technologies
Technology category | Technology | Storage medium | Storage duration | Efficiency (%) | Lifetime (years) | Heat capacity (kWh/m^3) | Cost (€/kWh) | Storage temperature (°C)
Sensible heat storage | Tank thermal energy storage (TTES) | Water | < days | 90-98 | 40-50 | 60-80 | 0.8-40 | ~60
Sensible heat storage | Solid-state thermal storage (SSTS) | Molten salt, concrete, crushed rocks | < days | 40-98 | 25 | Unknown | 10-100 | 200-600
Sensible heat storage | Underground thermal energy storage (UTES) - pit | Gravel and water mix | < months | 50-90 | 20-50 | 30-80 | 0.1-5 | 5-95
Sensible heat storage | Underground thermal energy storage (UTES) - borehole | Ground rock/ soil | < months | 70-90 | >30 | 15-30 | 2-16.5 | 5-90
Sensible heat storage | Underground thermal energy storage (UTES) - aquifer | Groundwater and ground material | < months | 65-95 | >30 | 30-40 | 0.1-2 | 10-60
Latent heat storage | Low temperature phase change material (LTPCM) | Paraffin wax or inorganic salt hydrates | < days | 75-90 | 15-20 | 30-100 | 10-350 | 60-80
Latent heat storage | High temperature phase change material (LTPCM) | Inorganic salts | < days | 75-90 | 15-20 | 30-100 | 10-80 | 150-250
Thermochemical heat storage | Thermochemical heat storage | Thermochemical materials | < months | 50-90 | >30 | 100-600 | 8-130 | -20-700
Key sources:
Codema and MullanGrid Consulting, “Poolbeg Sector Integration - Investigating synergies between the electricity, heat and hydrogen sectors,” SEAI, 2021.
Danish Energy Agency and Energinet, “Technology Data - Energy Storage,” Danish Energy Agency , Copenhagen, 2018.
Cardiff University, “Seasonal Storage of Heat in Boreholes,” UK Energy Research Centre, 2023.
H. Sadeghi, R. Jaliali and R. Martand Singh, “A review of borehole thermal energy storage and its integration into district heating systems,” Renewable and Sustainable Energy Reviews, vol. 192, p. 114236, 2024.
European Association for Storage of Energy, “Thermal Energy Storage,” European Association for Storage of Energy, Brussels, 2023.
Energy Storage with BVES, “Technology: Solid Medium Heat Storage,” International Energy Agency, 2024.
Sandia National Laboratories, “Thermal Energy Storage Technologies - Chapter 12,” in DOE Energy Storage Handbook, US Department of Energy, 2013.

## TES Illustrative Archetypes
Sustainable Energy Authority of Ireland - Flexible Electric Heating Technologies Report 2026
D3.1.1.3: Excel sheet summarising cost and performance parameters of storage technologies
Tables below summarises the size and cost of illustrative thermal energy storage (TES) archetypes across identified TES technologies and demand segments. As the cost of TES systems varies significantly by project (as shown on the TES Performance & Costs sheet), the archetypes costs are illustrative only.
Summary of cost and performance data for thermal energy storage technologies
Demand segment | TES capacity (kWh) | Duration (hours) | Comments and sources
Residential | 6.3 | 1 | Capacity based on Sunamp's Thermino 150 xPlus (https://sunamp.com/en-gb/thermino-xplus/), duration based on profile peakiness.
Commercial and public | 70 | 9 | Capacity based on Sunamp's Central Bank Mini (https://sunamp.com/en-gb/products/central-bank-mini/), duration based on profile peakiness.
Industry | 10000 | 10 | Highly dependent on site demand - illustrative magnitude based on examples of TES installed at industry site (https://www.kraftblock.com/projects/volt, https://www.rondo.com/)
District heating | 100000 | 100 | Highly dependent on site demand - illustrative magnitude based on case study of installed TES for district heating (for example: https://www.energy-storage.news/100mwh-sand-battery-goes-into-commercial-operation-in-finland/) - see WP3.1 report (D3.1.1.1) for other example case studies.
Summary of cost and performance data for thermal energy storage technologies
Technology category | Technology | Storage medium | Demand segment | Duration (hours) | Capacity (kWh) | Illustrative cost (€) | Illustrative lifetime (years) | Comments and sources
Sensible heat storage | Tank thermal energy storage (TTES) | Water | Residential | 1 | 6.3 | 1242 | 30 | Cost based on ERM/Element Energy Low Carbon Heat study for Kensa, lifetime based on European Association for Storage of Energy (https://ease-storage.eu/wp-content/uploads/2016/03/EASE_TD_HotWater.pdf)
Sensible heat storage | Tank thermal energy storage (TTES) | Water | Commercial and public | 9 | 70 | 4620 | 30 | Cost based on commercially available product from GRM, Cordivari, Thermal Earth (https://www.tanks-direct.co.uk/1500-litre-grp-hot-water-tank-insulated-50mm/p4317, https://www.loco2heat.co.uk/products/buffer-tanks-thermal-stores/thermal-store/cordivari-buffer-tank-puffer-vc-1500-litre/, https://www.thermalearth.co.uk/Products/Buffer_Tanks/TEHS1500), lifetime based on European Association for Storage of Energy (https://ease-storage.eu/wp-content/uploads/2016/03/EASE_TD_HotWater.pdf)
Sensible heat storage | Tank thermal energy storage (TTES) | Water | Industry | 10 | 10000 | 80000 | 50 | Cost based on upper case of large-scale water tank thermal energy storgae from the Danish Energy Agency
Sensible heat storage | Tank thermal energy storage (TTES) | Water | District heating | 100 | 100000 | 300000 | 50 | Cost based on central case of large-scale water tank thermal energy storgae from the Danish Energy Agency
Sensible heat storage | Solid-state thermal storage (SSTS) | Molten salt, concrete, crushed rocks | Residential | N/A | N/A | N/A | N/A | Considered unsuitable for typical residential buildings due to high temperatures
Sensible heat storage | Solid-state thermal storage (SSTS) | Molten salt, concrete, crushed rocks | Commercial and public | N/A | N/A | N/A | N/A | Considered unsuitable for typical commercial and public buildings due to high temperatures
Sensible heat storage | Solid-state thermal storage (SSTS) | Molten salt, concrete, crushed rocks | Industry | 10 | 10000 | 400000 | 25 | Cost based on upper limit of IEA Energy Storage Solid Medium Heat Storage factsheet with BVES
Sensible heat storage | Solid-state thermal storage (SSTS) | Molten salt, concrete, crushed rocks | District heating | 100 | 100000 | 4000000 | 25 | Cost based on upper limit of IEA Energy Storage Solid Medium Heat Storage factsheet with BVES
Sensible heat storage | Underground thermal energy storage (UTES) - pit | Gravel and water mix | Residential | N/A | N/A | N/A | N/A | Assumed unsuitable for residential building-level demand, as requires large thermal loads to be viable.
Sensible heat storage | Underground thermal energy storage (UTES) - pit | Gravel and water mix | Commercial and public | N/A | N/A | N/A | N/A | Assumed unsuitable for commercial and public building-level demand, as requires large thermal loads to be viable.
Sensible heat storage | Underground thermal energy storage (UTES) - pit | Gravel and water mix | Industry | 10 | 10000 | 50000 | 50 | Assumes upper limit of cost and temperature estimate provided by Codema
Sensible heat storage | Underground thermal energy storage (UTES) - pit | Gravel and water mix | District heating | 100 | 100000 | 500000 | 50 | Assumes upper limit of cost and temperature estimate provided by Codema
Sensible heat storage | Underground thermal energy storage (UTES) - borehole | Ground rock/ soil | Residential | N/A | N/A | N/A | N/A | Assumed unsuitable for residential building-level demand, as requires large thermal loads to be viable.
Sensible heat storage | Underground thermal energy storage (UTES) - borehole | Ground rock/ soil | Commercial and public | N/A | N/A | N/A | N/A | Assumed unsuitable for commercial and public building-level demand, as requires large thermal loads to be viable.
Sensible heat storage | Underground thermal energy storage (UTES) - borehole | Ground rock/ soil | Industry | 10 | 10000 | 20000 | 30 | Assumes upper limit of cost and temperature estimate provided by Codema
Sensible heat storage | Underground thermal energy storage (UTES) - borehole | Ground rock/ soil | District heating | 100 | 100000 | 200000 | 30 | Assumes upper limit of cost and temperature estimate provided by Codema
Sensible heat storage | Underground thermal energy storage (UTES) - aquifer | Groundwater and ground material | Residential | N/A | N/A | N/A | N/A | Assumed unsuitable for residential building-level demand, as requires large thermal loads to be viable.
Sensible heat storage | Underground thermal energy storage (UTES) - aquifer | Groundwater and ground material | Commercial and public | N/A | N/A | N/A | N/A | Assumed unsuitable for commercial and public building-level demand, as requires large thermal loads to be viable.
Sensible heat storage | Underground thermal energy storage (UTES) - aquifer | Groundwater and ground material | Industry | 10 | 10000 | 20000 | 30 | Assumes upper limit of cost and temperature estimate provided by Codema
Sensible heat storage | Underground thermal energy storage (UTES) - aquifer | Groundwater and ground material | District heating | 100 | 100000 | 200000 | 30 | Assumes upper limit of cost and temperature estimate provided by Codema
Latent heat storage | Low temperature phase change material (LTPCM) | Paraffin wax or inorganic salt hydrates | Residential | 1 | 6.3 | 5054 | 20 | Cost based on the Sunamp Thermino 150 xPlus (https://www.ecosmartheat.co.uk/heat-pumps.html)
Latent heat storage | Low temperature phase change material (LTPCM) | Paraffin wax or inorganic salt hydrates | Commercial and public | 9 | 70 | 28079 | 20 | Cost based on the larger Sunamp Central Bank Mini, with marginal cost 50% of residential Thermino 150 xPlus as it is an order of magnitude bigger.
Latent heat storage | Low temperature phase change material (LTPCM) | Paraffin wax or inorganic salt hydrates | Industry | 10 | 10000 | 1000000 | 20 | Cost based on upper limit of IEA Energy Storage Low Temperature Latent Heat Storage factsheet with BVES
Latent heat storage | Low temperature phase change material (LTPCM) | Paraffin wax or inorganic salt hydrates | District heating | 100 | 100000 | 10000000 | 20 | Cost based on upper limit of IEA Energy Storage Low Temperature Latent Heat Storage factsheet with BVES
Latent heat storage | High temperature phase change material (LTPCM) | Inorganic salts | Residential | N/A | N/A | N/A | N/A | Considered unsuitable for typical residential buildings due to high temperatures
Latent heat storage | High temperature phase change material (LTPCM) | Inorganic salts | Commercial and public | N/A | N/A | N/A | N/A | Considered unsuitable for typical commercial and public buildings due to high temperatures
Latent heat storage | High temperature phase change material (LTPCM) | Inorganic salts | Industry | 10 | 10000 | 800000 | 20 | Cost based on upper limit of IEA Energy Storage High Temperature Latent Heat Storage factsheet with BVES
Latent heat storage | High temperature phase change material (LTPCM) | Inorganic salts | District heating | 100 | 100000 | 8000000 | 20 | Cost based on upper limit of IEA Energy Storage High Temperature Latent Heat Storage factsheet with BVES
Thermochemical heat storage | Thermochemical heat storage | Thermochemical materials | Residential | N/A | N/A | N/A | N/A | Considered unsuitable due to low TRL, with limited to no demonstration of systems for residential and commercial applications
Thermochemical heat storage | Thermochemical heat storage | Thermochemical materials | Commercial and public | N/A | N/A | N/A | N/A | Considered unsuitable due to low TRL, with limited to no demonstration of systems for residential and commercial applications
Thermochemical heat storage | Thermochemical heat storage | Thermochemical materials | Industry | 10 | 10000 | 1300000 |  | Cost based on upper limit of IEA Energy StorageThermochemical Heat Storage by Sorption factsheet with BVES. Low TRL, so costs highly uncertain
Thermochemical heat storage | Thermochemical heat storage | Thermochemical materials | District heating | 100 | 100000 | 13000000 |  | Cost based on upper limit of IEA Energy StorageThermochemical Heat Storage by Sorption factsheet with BVES. Low TRL, so costs highly uncertain